## 050-L-PPN-55001-002-RA-CS
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Call-out | [1] 050-L-PPN-55001-002-Model | Edgardo | It is suggested to exclude the temporary construction fence from this drawing, which is intended to show only the permanent installations
2 |  | [1] 050-L-PPN-55001-002-Model | AutoCAD SHX Text | The present document or drawing is property of TECHNIP ITALY S.p.A. and shall not, under any circumstances, be totally or partially, directly or indirectly, transferred, reproduced, copied, disclosed or used, without its prior written consent, for any purpose and in any way other than that for which it is specifically furnished or outside the extent of the agreed upon right of use.
3 | Call-out | [1] 050-L-PPN-55001-002-Model | Ahmed Ali | ensure that all valves, equipment are accessible for operation and maintenance
4 | Callout | [1] 050-L-PPN-55001-002-Model | Erwin.Lugue | Verify sufficiency of bundwall for spill control
5 | Callout | [1] 050-L-PPN-55001-002-Model | Erwin.Lugue | Include all symbologies & abbreviations
6 | Call-out | [1] 050-L-PPN-55001-002-Model | MAK | General Comment: Use DD.MM.YYYY format for the date, e.g. 25.05.2018
7 | Text Box | [1] 050-L-PPN-55001-002-Model | Erwin.Lugue | relative
8 | Callout | [1] 050-L-PPN-55001-002-Model | Berik.Nurbolatov | All dimensions and distances for reference purpose should be shown.
9 | Callout | [1] 050-L-PPN-55001-002-Model | Erwin.Lugue | Missing channel/ open drains, slopes, & sump collector
10 | Call-out | [1] 050-L-PPN-55001-002-Model | Edgardo | The bundwalls shall be provided with sufficient number of access stairs for personnel. This comment applies to all bundwalls
11 | Callout | [1] 050-L-PPN-55001-002-Model | Abdul Rahim | please refer to comments on sheet 1
12 | Call-out | [1] 050-L-PPN-55001-002-Model | Mahdi Ali | To be finalized
13 | Callout | [1] 050-L-PPN-55001-002-Model | Erwin.Lugue | HPP Level?
14 | Callout | [1] 050-L-PPN-55001-002-Model | Erwin.Lugue | Radius?
15 | Callout | [1] 050-L-PPN-55001-002-Model | Erwin.Lugue | Missing draw-off sumps
16 | Call-out | [1] 050-L-PPN-55001-002-Model | Ahmed Marhoon | Concerns on meeting the spacing requirements between the SS and the tank bund wall to be addressed by the contractor.
17 | Text Box | [1] 050-L-PPN-55001-002-Model | Erwin.Lugue | slope?
18 | Callout | [1] 050-L-PPN-55001-002-Model | Erwin.Lugue | Verify for additional access & egress
19 | Callout | [1] 050-L-PPN-55001-002-Model | Erwin.Lugue | Missing drain slopes, & sump collectors
20 | Text Box | [1] 050-L-PPN-55001-002-Model | Erwin.Lugue | Indicate all elevations in the section
21 |  | [1] 050-L-PPN-55001-002-Model | AutoCAD SHX Text | - C/Arapiles 14, Madrid, Spain
22 | Callout | [1] 050-L-PPN-55001-002-Model | Erwin.Lugue | Orientation of Northing pointing upward in reference to key plan. For angle conversion, refer to BMP-CON-LET-00047
23 | Call-out | [1] 050-L-PPN-55001-002-Model | MAK | Delete. This is for Bapco use.
24 | Call-out | [1] 050-L-PPN-55001-002-Model | MAK | Change L to A which is the correct Material Class for Plot Plan.
25 | Text Box | [1] 050-L-PPN-55001-002-Model | Erwin.Lugue | Clarify scope of involved work packages in this unit
26 | Callout | [1] 050-L-PPN-55001-002-Model | Berik.Nurbolatov | Please make sure that 3 off decimals are used
27 | Callout | [1] 050-L-PPN-55001-002-Model | Erwin.Lugue | H=?
28 | Cloud+ | [1] 050-L-PPN-55001-002-Model | Ahmed Marhoon | Contractor to check and confirm the building number. Is this the Satellite Rack Room number 163RR01?
29 | Callout | [1] 050-L-PPN-55001-002-Model | Erwin.Lugue | Walkways missing
30 | Callout | [1] 050-L-PPN-55001-002-Model | Erwin.Lugue | H=?
31 | Call-out | [1] 050-L-PPN-55001-002-Model | MAK | Delete F and never use prefixes for Unit Nos.
32 | Callout | [1] 050-L-PPN-55001-002-Model | Erwin.Lugue | Not TOS?
33 | Call-out | [1] 050-L-PPN-55001-002-Model | Abdulaziz | Lube oil & chemical shelter shall be provided as per BMPS vol 2, sec 6
34 | Text Box | [1] 050-L-PPN-55001-002-Model | Erwin.Lugue | Missing firefighting facilities, i.e. fire monitors
35 | Callout | [1] 050-L-PPN-55001-002-Model | Erwin.Lugue | Should refer to TOS
36 | Text Box | [1] 050-L-PPN-55001-002-Model | Erwin.Lugue | HPP Elevations? Paving type?
37 | Text Box | [1] 050-L-PPN-55001-002-Model | Erwin.Lugue | relative
38 | Call-out | [1] 050-L-PPN-55001-002-Model | Abdulaziz | Sufficient space shall be provided for regular maintenance with minimum disturbance to the piping and adjacent equipment during major overhaul.
39 | Callout | [1] 050-L-PPN-55001-002-Model | Erwin.Lugue | H=?
40 | Text Box | [1] 050-L-PPN-55001-002-Model | Erwin.Lugue | Missing dimensions, & coordinates to locate equipments & structures
41 | Call-out | [1] 050-L-PPN-55001-002-Model | MAK | Delete U372
42 | Text Box | [1] 050-L-PPN-55001-002-Model | Erwin.Lugue | corresponds
43 | Callout | [1] 050-L-PPN-55001-002-Model | Erwin.Lugue | H=?
44 | Callout | [1] 050-L-PPN-55001-002-Model | Berik.Nurbolatov | Plot plans shall be dimensioned in metric units (mm) of linear measurement (refer BMPS A8 ‘General guidelines of Plot plan layout Part B Appendix B1
45 | Callout | [1] 050-L-PPN-55001-002-Model | Berik.Nurbolatov | The road center line thickness should be reduced.
46 | Text Box | [1] 050-L-PPN-55001-002-Model | MAK | General Comment: The latest drawing borders have been submitted to JV Directorate on April 2018. Please use the latest drawing borders that are part of the Homogenisation Procedure.
47 | Text Box | [1] 050-L-PPN-55001-002-Model | Erwin.Lugue | slope?
48 | Text Box | [1] 050-L-PPN-55001-002-Model | Edgardo | Please show the location of the tank stairs, including the landing area. This comment applies to all tanks.
49 | Text Box | [1] 050-L-PPN-55001-002-Model | Abdulaziz | Proper study shall be carried out to demonstrate the easy access to perform maintenance activities utilizing forklift to mobilize the requirement
50 | Callout | [1] 050-L-PPN-55001-002-Model | Erwin.Lugue | TOS? Sleeper? Steel?
51 | Callout | [1] 050-L-PPN-55001-002-Model | Erwin.Lugue | Not TOS ? Pipe resting on embedded plate?
52 | Callout | [1] 050-L-PPN-55001-002-Model | Erwin.Lugue | Missing elevation, & coordinates in road intersections- typ. comments
53 | Arrow | [1] 050-L-PPN-55001-002-Model | MAK
54 | Callout | [1] 050-L-PPN-55001-002-Model | Berik.Nurbolatov | Please follow unique legend for "section view ". Refer to the "arrow "used in other unit plot plans.
55 | Callout | [1] 050-L-PPN-55001-002-Model | Erwin.Lugue | Radius?
56 | Callout | [1] 050-L-PPN-55001-002-Model | alexis.martinez | General: All Equipment Number need to be updated as per the new numbering provided by owner.
57 | Text Box | [1] 050-L-PPN-55001-002-Model | Berik.Nurbolatov | Please mention HPP grade El. relative to site.
58 | Callout | [1] 050-L-PPN-55001-002-Model | Erwin.Lugue | Provide section
59 | Callout | [1] 050-L-PPN-55001-002-Model | Berik.Nurbolatov | Please follow unique legend for "section view ". Refer to the "arrow "used in other unit plot plans.
60 |  | [1] 050-L-PPN-55001-002-Model | AutoCAD SHX Text | THIS DRAWING
61 | Callout | [1] 050-L-PPN-55001-002-Model | Erwin.Lugue | Reorganize frame grid numbering system