## 050-P-INX-55001-001-RA-CS
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Text Box | 1 | MAK | UNIT 050 -
2 | Text Box | 1 | MAK | General Comment: Use the latest document template that is part of the Homogenisation Procedure.
3 | Callout | 1 | Sankara | Use Unit Number according to Project Tagging system
4 | Callout | 2 | Sankara | Call as Equipment Tag Number: Typical
5 | Text Box | 3 | Sankara | Indicate all loads in Tankfarm to be connected to the existing 60 Hz system, either as part of this document or as separate listing.
6 | Cloud+ | 3 | Mohamed Ayyash | Align
7 | Text Box | 4 | Sankara | For typical comments, refer to Electrical Consumer List Document for 2HCU ( Unit 019)
8 | Text Box | 4 | Ahmed.Marhoon | Instrumentation and Control Comments. 1. Contractor to ensure that all power supply consumers for the instrumentation and control are detailed/included in compliance with the applicable BMPS specifications such as J1, J14, P1 ...etc. All redundant power supplies (including UPS & non-UPS) for safety and non-safety related to be considered/added (DCS, ESD, GAS, FAS, MCM, PLC ...etc) in the list. 2. All power supply consumers for field standalone control systems, if any, to be considered/added. 3. Satellite Rack Rooms details (including building numbers) to be updated based on the latest SRR building design/numbers. 4. List to be updated based on the detail engineering development to include any new requirements based on selected instrument models/vendors such field instruments requiring external 110 VAC power supply. 5. The development in the new refinery centralized control building shall be considered in this list. 6. Equipment tagging to be updated based on the final agreement on Booster pumps plant prefix numbers.
9 | Call-out | 4 | Mahdi Ali | Remove 'X'
10 | Call-out | 4 | Mahdi Ali | Unit number shall be 3 digits only
11 | Call-out | 4 | Mahdi Ali | Incorrect tag for substation
12 | Cloud+ | 5 | CK Samy | unit no. shall be corrected
13 | Callout | 5 | Sankara | This is incorrect. Why Operation Building feeders are used only during start up
14 | Call-out | 5 | CK Samy | Segregate load based on 50Hz or 60Hz supply source.
15 | Text Box | 5 | Sankara | Include missing loads such as AC UPS for ESD Systems
16 | Call-out | 6 | CK Samy | Indicate supply bus of power supply
17 | Cloud+ | 6 | CK Samy | unit no. shall be corrected