## 050-Q-PED-55691-002-RA-CS
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Cloud+ | 1 | Erwin.Lugue | What thickness, & material?
2 | Callout | 1 | Erwin.Lugue | Indicate surface finish, concrete protection coating below grade as per BPMS-M2, & BPMS-Q-50701
3 | Cloud+ | 1 | Erwin.Lugue | Check minimum spacing between anchor bolts as per ASCE
4 | Callout | 1 | Erwin.Lugue | Projection of anchor bolts?
5 | Text Box | 1 | Erwin.Lugue | References: Road & paving plan Piping Layout DWGs Culvert Drawings
6 | Cloud+ | 1 | Erwin.Lugue | What material? Anchor stud bolts?
7 | Cloud+ | 1 | Erwin.Lugue | Why is the footing continuous?
8 | Cloud+ | 1 | Erwin.Lugue | Width of hooks
9 | Callout | 1 | Erwin.Lugue | Specify dimension of anchor bolt embedment
10 | Cloud+ | 1 | Erwin.Lugue | Check minimum anchor bolt edge distance as per ASCE
11 | Callout | 1 | Erwin.Lugue | Welding?
12 | Callout | 1 | Mahdi Ali | MATERIAL CLASS FOR PLOT PLANS IS 'A' AND NOT 'L'. CHANGE THIS AND ALL THE REFERENCES ACCORDINGLY
13 | Text Box | 1 | Erwin.Lugue | Provide all the abbreviations.
14 | Callout | 1 | Erwin.Lugue | Indicate surface finish, concrete protection coating surface grade as per BPMS-M2, & BPMS-Q-50701
15 | Callout | 1 | Berik.Nurbolatov | What does "J" stand for? Cjange it to dimension data or put a reference note.
16 | Text Box | 1 | Mahdi Ali | USE THE UPDATED DRAWING BORDER THAT IS PART OF THE HOMOGENIZATION PROCEDURE
17 | Cloud+ | 1 | Erwin.Lugue | Horizontal reinforcements far from the vertical bars
18 | Cloud+ | 1 | Erwin.Lugue | What material? Anchor stud bolts? Provide embedment length
19 | Cloud+ | 1 | Erwin.Lugue | Extend the lean concrete 50mm
20 | Text Box | 1 | Erwin.Lugue | All exposed concrete edges shall be chamfered, BPMS-M2
21 | Cloud+ | 1 | Erwin.Lugue | Orientation not as per key plan
22 | Callout | 1 | Berik.Nurbolatov | Provide H.P.P number/data
23 | Callout | 1 | Erwin.Lugue | Construction joint detail?
24 | Callout | 1 | Erwin.Lugue | Anchor bolt projection?
25 | Cloud+ | 1 | Erwin.Lugue | Update with the latest plot plan
26 | Cloud+ | 1 | Erwin.Lugue | Top of steel plate?
27 | Text Box | 1 | Erwin.Lugue | Provide overall plot plan
28 | Cloud+ | 1 | Erwin.Lugue | Extend the lean concrete 50mm
29 | Cloud+ | 1 | Erwin.Lugue | Use closed type ties
30 | Callout | 1 | Erwin.Lugue | Indicate surface finish, concrete protection coating surface grade as per BPMS-M2, & BPMS-Q-50701
31 | Cloud+ | 1 | Erwin.Lugue | What are these ties for?
32 | Callout | 1 | Erwin.Lugue | Plant Northing?
33 | Callout | 1 | Mahdi Ali | 4
34 | Callout | 1 | Erwin.Lugue | Specify dimension of anchor bolt embedment
35 | Text Box | 1 | Erwin.Lugue | General comment: This drawing needs to be resubmitted with the calculation reports and could not be properly reviewed/ or issued for construction until the approval of the following basic documents: 1) Basis of Design for Structures & Foundations 2) Final Geotechnical Investigations & Recommendation reports 3) Pile/Deep Foundations Design Criterias, Specifications, and Tests (If applicable) 4) Plot plan 5) Piping Layout
36 | Callout | 1 | Erwin.Lugue | Indicate surface finish, concrete protection coating below grade as per BPMS-M2, & BPMS-Q-50701
37 | Callout | 1 | Erwin.Lugue | Anchor bolt layout?
38 | Cloud+ | 1 | Erwin.Lugue | What is this pedestal type? Should refer to the typical section
39 | Cloud+ | 1 | Erwin.Lugue | Check with the standard tie requirements as per BPMS-Q1, & ASCE anchor bolt design for petrochemical facilities
40 | Cloud+ | 1 | Erwin.Lugue | Millimeters
41 | Callout | 1 | Erwin.Lugue | Provide plan view of pedestal reinforcement arrangement