## 050-S-BLD-55001-001-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Cloud+ | 1 | MAK | 163
2 | Cloud+ | 1 | MAK | 163 - 8AC / FB PUMPS SRR
3 | Call-out | 1 | Bachir M | All connections between Control & Safety Systems and other systems shall comply with the requirements of BMPS-J40
4 | Text Box | 1 | Omran A | Button
5 | Cloud+ | 1 | MAK | Change to 163SRR01
6 | Cloud+ | 1 | MAK | Change to: 163SRR01
7 | Cloud+ | 1 | MAK | Change to: 934SSTR01
8 | Text Box | 1 | Omran A | Dual serial link between DCS and ESD shall be provided.
9 | Text Box | 1 | MAK | General Comment: All the texts in drawings shall be searchable and in UPPERCASE. Text fonts and styles shall be as per BMPS-A8.
10 | Text Box | 1 | MAK | General Comment: Refer to the latest Building Numbers for the correct numbers.
11 | Text Box | 1 | Ahmed.Marhoon | In addition to the comments on this document, refer to comments provided on CWT and 2HCU equivalent drawings.
12 | Text Box | 1 | CK Samy | indicate all reference drawing and documents
13 | Call-out | 1 | CK Samy | indicate battery room explosion proof heat detector, manual call point, alarm bell etc.,
14 | Call-out | 1 | CK Samy | Indicate Emergency generator FACP with heat detector, manual call point ,alarm bell etc., with connectivity to rack room F&G system
15 | Call-out | 1 | CK Samy | Indicate MUX prior to DCS
16 | Call-out | 1 | CK Samy | indicate room room battery and HVAC fire detectors connected to FACP
17 | Call-out | 1 | CK Samy | indicate room room battery and HVAC gas detectors connected to GAS
18 | Call-out | 1 | CK Samy | Indicate substation building Gas Alarm system for the following with connectivity to DCS 1. battery room H2 gas detector 2. HVAC system H2S and HC detectors
19 | Text Box | 1 | Ahmed Habib | Refer to comments shown in Transmittal : MOC-TRI-00435