## 050-S-GAD-55003-001-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Text Box | 1 | giovanny.rodriguez | Add columns to check all equipment & supports (e.g. legs, columns, skirt, saddles) affected or requiring for fire proofing & the corresponding thk
2 | Text Box | 1 | giovanny.rodriguez | add separate columns for equipment content & for hazard category (i.e. fire hazard or fire exposure)
3 | Text Box | 1 | Ahmed.Marhoon | Based on this FEE, critical instruments (such as solenoid valves, junction boxes ... etc) and emergency equipment (such as MOVs) to be provided with the necessary protection means against early failure due to fire. All single-pair cables and wiring within the FEE (regardless of elevation) to be of inherently fire-resistant type. For multi-pair cables, fireproof coating to be provided on exposed sections from ground to the respective JB where the JB will also be provided with fireproofing materials. Refer to BMPS-J-175470 for details of FIREPROOFING OF MOV, CABLE TRAY, CABLE AND JUNCTION BOX. In general, criteria specified under section 5.7 of BMPS-M6 to be applied. Necessary note to be added to this drawing for compliance.
4 | Callout | 1 | Chandrahasan D | ENVELOPE
5 | Cloud+ | 1 | MAK | GENERAL ARRANGEMENT DRAWING
6 | Cloud+ | 1 | MAK | General Comment: All dimensions are in MILLIMETER. As per BMPS-A1 Section 10.2.
7 | Callout | 1 | giovanny.rodriguez | HAZARDOUS
8 | Callout | 1 | Chandrahasan D | In case of spill, the trench have potential for fire. Verify the trench area to be included in FEE.
9 | Callout | 1 | Mahdi Ali | QUOTE BAPCO NUMBER INSTEAD OF THE FEED NUMBER
10 | Call-out | 1 | Ahmed.Marhoon | Should this be changed to EPC reference?
11 | Text Box | 1 | giovanny.rodriguez | SHOW 9m OF VERT. FIRE EXPOSED AREA
12 | Text Box | 1 | Chandrahasan D | Show OWS MHs and vents and verify their impact on FEE extent
13 | Text Box | 1 | giovanny.rodriguez | TANKS GAD SHALL BE LISTYED AS REFERENCES
14 | Call-out | 1 | Edgardo | These equipment belong to Uni 372 and would need to be shown in another document specific for Unit 372; It is noted that current document is for Unit 050
15 | Callout | 1 | Chandrahasan D | Verify Fire break requirements on pipe trench and show in the drawing if required.