## 050-S-GAD-55003-002-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Text Box | 1 | Berik.Nurbolatov | 0
2 | Text Box | 1 | Berik.Nurbolatov | 0
3 | Text Box | 1 | Berik.Nurbolatov | 0
4 | Cloud+ | 1 | MAK | 934P1000A
5 | Cloud+ | 1 | MAK | 934P1000B
6 | Cloud+ | 1 | MAK | 934P1800A
7 | Cloud+ | 1 | MAK | 934P1800B
8 | Cloud+ | 1 | MAK | 934P1900A 934T1900A
9 | Cloud+ | 1 | MAK | 934P1900B 934T1900B
10 | Cloud+ | 1 | MAK | 934P1900C
11 | Cloud+ | 1 | MAK | 934P2100A 934T2100A
12 | Cloud+ | 1 | MAK | 934P2100B 934T2100B
13 | Cloud+ | 1 | MAK | 934P2100C
14 | Text Box | 1 | giovanny.rodriguez | Add columns to check all equipment & supports (e.g. legs, columns, skirt, saddles) affected or requiring for fire proofing & the corresponding thk
15 | Text Box | 1 | giovanny.rodriguez | add separate columns for equipment content & for hazard category (i.e. fire hazard or fire exposure)
16 | Text Box | 1 | Ahmed.Marhoon | Based on this FEE, critical instruments (such as solenoid valves, junction boxes ... etc) and emergency equipment (such as MOVs) to be provided with the necessary protection means against early failure due to fire. All single-pair cables and wiring within the FEE (regardless of elevation) to be of inherently fire-resistant type. For multi-pair cables, fireproof coating to be provided on exposed sections from ground to the respective JB where the JB will also be provided with fireproofing materials. Refer to BMPS-J-175470 for details of FIREPROOFING OF MOV, CABLE TRAY, CABLE AND JUNCTION BOX. In general, criteria specified under section 5.7 of BMPS-M6 to be applied. Necessary note to be added to this drawing for compliance.
17 | Cloud+ | 1 | MAK | Change to: 934P1000A/B 934P2100A/B/C 934P1900A/B/C 934P1800A/B 934T2100A/B 934T1900A/B Pay attention to the updated and correct equipment tag nos.
18 | Callout | 1 | Berik.Nurbolatov | DISPLAY FIRE EXPOSED ZONE ON SECTION VIEW.
19 | Cloud+ | 1 | MAK | GENERAL ARRANGEMENT DRAWING
20 | Cloud+ | 1 | MAK | General Comment: All dimensions are in MILLIMETER. As per BMPS-A1 Section 10.2.
21 | Callout | 1 | Berik.Nurbolatov | HAZARDOUS
22 | Callout | 1 | Mahdi Ali | QUOTE BAPCO NUMBER INSTEAD OF THE FEED NUMBER
23 | Cloud+ | 1 | MAK | Refer to the agreed Buildings Names & Numbers. Change it to 934SSTR01
24 | Text Box | 1 | giovanny.rodriguez | SHOW 9m OF VERT. FIRE EXPOSED AREA
25 | Text Box | 1 | Chandrahasan D | Show OWS MHs and vents and verify their impact on FEE extent
26 | Text Box | 1 | giovanny.rodriguez | TANKS GAD SHALL BE LISTYED AS REFERENCES
27 | Callout | 1 | Berik.Nurbolatov | The background data(drawing) should be up to date. The elevation data should be three decimal units.
28 | Callout | 1 | Chandrahasan D | Verify Fire proofing requirement of trench. show fire breaks to contain spils