## 050-S-PED-55810-001-RA-CS
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Callout | 1 | Erwin.Lugue | Detail of construction joint?
2 | Callout | 1 | Erwin.Lugue | Provide reinforcement hooks/ anchor curtailment
3 | Cloud+ | 1 | Erwin.Lugue | This additional reinforcement detail is far from the interior corner. Also the diameter should be similar with the main reinforcement
4 | Cloud+ | 1 | MAK | 0.35417
5 | Callout | 1 | Erwin.Lugue | Where is the drain?
6 | Text Box | 1 | mohamed.alaradi | 1- Road access for heavy machinery not shown 2- Bund wall sewer system/ drainage not shown 3- Section-A concrete wall is 2 meter high. It may be a confined space in some locations especially the corners. 4- Bund volume for the two tanks shall be matching with the NFPA30 STD size requirements. 5- Tank berm / tank foundation level difference are not shown 6- fire fighting facilities / fire hydrants / fire monitors and foam pipes / locations not shown.
7 | Text Box | 1 | Erwin.Lugue | Tank coordinates?
8 | Callout | 1 | Mahdi Ali | MATERIAL CLASS FOR PLOT PLANS IS 'A' AND NOT 'L'. CHANGE THIS AND ALL THE REFERENCES ACCORDINGLY.
9 | Callout | 1 | Erwin.Lugue | Specify surface finishes, below ground & surface grade concrete protection as per BPMS-M2
10 | Callout | 1 | Erwin.Lugue | Specify surface finishes, below ground & surface grade concrete protection as per BPMS-M2
11 | Callout | 1 | Erwin.Lugue | Orientation not as per key plan
12 | Text Box | 1 | Mahdi Ali | USE THE LATEST DRAWING BORDER THAT IS PART OF THE HOMOGENIZATION PROCEDURE
13 | Text Box | 1 | Erwin.Lugue | General comment: This drawing needs to be resubmitted with the calculation reports and checked only for general conformance. The drawing cannot be issued for construction until the approval of the following basic documents: 1) Basis of Design for Structures & Foundations 2) Final Geotechnical Investigations & Recommendation reports 3) Pile/Deep Foundations Design Criterias, Specifications, and Tests (If applicable) 4) Plot plan 5) Piping Layout
14 | Callout | 1 | Mahdi Ali | 1
15 | Cloud+ | 1 | Erwin.Lugue | Update key plan with latest plot plan version
16 | Callout | 1 | Erwin.Lugue | Gravel?
17 | Text Box | 1 | Erwin.Lugue | Provide location & foundations of stairs
18 | Callout | 1 | Erwin.Lugue | Location of pit collector & surface drainage?
19 | Text Box | 1 | Erwin.Lugue | Provide outline of the tank foundations
20 | Text Box | 1 | Erwin.Lugue | Indicate in plans the height of walls (H)
21 | Cloud+ | 1 | Erwin.Lugue | Why open?
22 | Text Box | 1 | Erwin.Lugue | Add reference DWGs: 1) Grading & Paving Plan 2) Tank Foundation DWGs 3) Piping Layout DWGs
23 | Text Box | 1 | Erwin.Lugue | Provide the HPP or FGL levels inside and outside the walls
24 | Callout | 1 | Erwin.Lugue | Where is the road access detail?
25 | Text Box | 1 | Erwin.Lugue | Not to provide too many sizes of reinforcements
26 | Callout | 1 | Erwin.Lugue | Where is the walkway elevation & finish grade level outside the wall?
27 | Text Box | 1 | Erwin.Lugue | Provide all the abbreviations
28 | Cloud+ | 1 | Erwin.Lugue | Verify thickness for reinforcement anchorage development length
29 | Text Box | 1 | Erwin.Lugue | Provide details & location of construction & expansion joints
30 | Text Box | 1 | Erwin.Lugue | Provide overall plot plan
31 | Callout | 1 | Erwin.Lugue | Provide lean concrete