## 050-S-PED-55811-001-RA-CS
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Callout | 1 | Erwin.Lugue | Provide reinforcement hooks/ anchor curtailment
2 | Callout | 1 | Erwin.Lugue | Where is the walkway elevation & finish grade level outside the wall?
3 | Cloud+ | 1 | MAK | 0.35417
4 | Callout | 1 | Erwin.Lugue | Provide lean concrete
5 | Callout | 1 | Erwin.Lugue | Is this part of wall exposed?
6 | Callout | 1 | Erwin.Lugue | Where is the walkway elevation & finish grade level outside the wall?
7 | Cloud+ | 1 | Erwin.Lugue | Verify thickness for reinforcement anchorage development length
8 | Text Box | 1 | Erwin.Lugue | Provide details & location of construction & expansion joints
9 | Callout | 1 | Erwin.Lugue | Location of pit collector & surface drainage?
10 | Text Box | 1 | Mahdi Ali | USE THE LATEST DRAWING BORDER THAT IS PART OF THE HOMOGENIZATION PROCEDURE
11 | Text Box | 1 | Erwin.Lugue | Alternate vertical lapping of reinforcements
12 | Cloud+ | 1 | Erwin.Lugue | Different elevations of walls? Provide section & details
13 | Text Box | 1 | Erwin.Lugue | Provide outline of the tank foundations
14 | Callout | 1 | Erwin.Lugue | Specify surface finishes, below ground & surface grade concrete protection as per BPMS-M2
15 | Callout | 1 | Erwin.Lugue | This outside part of stepped wall not to be exposed
16 | Text Box | 1 | Erwin.Lugue | Not to provide too many sizes of reinforcements
17 | Text Box | 1 | Erwin.Lugue | Provide location & foundations of stairs
18 | Cloud+ | 1 | Erwin.Lugue | This additional reinforcement detail is far from the interior corner. Also the diameter should be similar with the main reinforcement
19 | Text Box | 1 | Erwin.Lugue | Indicate in plans the height of walls (H)
20 | Text Box | 1 | Erwin.Lugue | Tank coordinates?
21 | Cloud+ | 1 | Erwin.Lugue | Update key plan with latest plot plan version
22 | Callout | 1 | Erwin.Lugue | Detail of construction joint?
23 | Text Box | 1 | Erwin.Lugue | Provide the HPP or FGL levels inside and outside the walls
24 | Text Box | 1 | Erwin.Lugue | Provide overall plot plan
25 | Text Box | 1 | Erwin.Lugue | Add reference DWGs: 1) Grading & Paving Plan 2) Tank Foundation DWGs 3) Piping Layout DWGs
26 | Callout | 1 | Erwin.Lugue | Provide reinforcement hooks/ anchor curtailment
27 | Callout | 1 | Erwin.Lugue | Specify surface finishes, below ground & surface grade concrete protection as per BPMS-M2
28 | Callout | 1 | Erwin.Lugue | Detail of construction joint?
29 | Text Box | 1 | Erwin.Lugue | Provide all the abbreviations
30 | Callout | 1 | Mahdi Ali | 1
31 | Callout | 1 | Erwin.Lugue | All exposed concrete shall be chamfered as per BPMS-M2
32 | Cloud+ | 1 | Erwin.Lugue | Why open?
33 | Callout | 1 | Erwin.Lugue | Specify surface finishes, below ground & surface grade concrete protection as per BPMS-M2
34 | Callout | 1 | Erwin.Lugue | Where is the drain?
35 | Text Box | 1 | Erwin.Lugue | General comment: This drawing needs to be resubmitted with the calculation reports and checked only for general conformance. The drawing cannot be issued for construction until the approval of the following basic documents: 1) Basis of Design for Structures & Foundations 2) Final Geotechnical Investigations & Recommendation reports 3) Pile/Deep Foundations Design Criterias, Specifications, and Tests (If applicable) 4) Plot plan 5) Piping Layout
36 | Cloud+ | 1 | Erwin.Lugue | Ensure in the calculation the minimum anchorage & required lap length
37 | Callout | 1 | Erwin.Lugue | Orientation not as per key plan
38 | Callout | 1 | Mahdi Ali | MATERIAL CLASS FOR PLOT PLANS IS 'A' AND NOT 'L'. CHANGE THIS AND ALL THE REFERENCES ACCORDINGLY.
39 | Text Box | 1 | mohamed.alaradi | A- three meter high concrete bund wall may cause confined space area. This has to be reviewed against NFPA30 STD or equivalent . B- fire monitors / facilities not shown C- Road access for heavy machinery not shown D- Drainage system in the bund wall not shown E- Tank foundation slope / bund area level difference not shown.