## 051-A-PID-00004-001-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Callout | 1 | Abdul Rahim | improve title
2 | Text Box | 1 | MAK | 051M0001A
3 | Text Box | 1 | MAK | 051M0001B
4 | Callout | 1 | Mahdi Ali | ADD PID REFERENCE NO.
5 | Callout | 1 | Abdul Rahim | add: #1 & 2 berths
6 | Callout | 1 | Abdul Rahim | advise size of valve, if 16" then it might be better to be upstream of check valve
7 | Callout | 1 | Abdul Rahim | Advise the location of these switches
8 | Callout | 1 | Abdul Rahim | assume it be opened manually
9 | Callout | 1 | Abdul Rahim | Change title as per first sheet
10 | Callout | 1 | Abdul Rahim | change to meters
11 | Callout | 1 | Francis L | Clarify means to connect to Owner DCS.
12 | Callout | 1 | Francis L | Clarify whether a local field indicator readable at grade, is required.
13 | Callout | 1 | Francis L | Consider indicating brief function as Note.
14 | Callout | 1 | Abdul Rahim | discuss isolation requirement
15 | Callout | 1 | Abdul Rahim | Explain why no by pass
16 | Callout | 1 | Abdul Rahim | explain why no by pass on low range
17 | Text Box | 1 | MAK | General Comment to be applied to all P&IDs: As per BMPS-A8, Section 8.4.3, Drivers Tag Nos. e.g. Motors/Turbines shall always be inserted in all P&IDs and placed below the parent equipment no. e.g. Pump/Fan/Mixer/Cooler where possible. Motor FinFan tag nos. shall always be shown where applicable.
18 | Callout | 1 | Francis L | Indicate brief function in Note.
19 | Callout | 1 | Francis L | Indicate function as Note
20 | Callout | 1 | Francis L | management
21 | Callout | 1 | Francis L | Not soft signals.
22 | Callout | 1 | Abdul Rahim | Pls discuss requirement for by pass
23 | Call-out | 1 | Edgardo | should be C3/C4
24 | Callout | 1 | Abdul Rahim | where will be the location of the valve