## 051-A-PID-00013-001-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Callout | 1 | Francis L | As per BMPS-J3 indicate tag suffix with 2 letters ie. AA. Applies to all other similar tags.
2 | Callout | 1 | Francis L | Can valves be tested online?
3 | Callout | 1 | Francis L | Clarify function and insert as Note.
4 | Callout | 1 | Francis L | Clarify function of signal.
5 | Callout | 1 | Francis L | FF signal.
6 | Call-out | 1 | Edgardo | Globe valves need to be included in pipe spec C9M or B9m, as these are shown on the bypass valves.
7 | Call-out | 1 | Edgardo | Please clarify which line will be used for hot gas purging of the liquid lines which is carried out after the loading operation
8 | Call-out | 1 | Edgardo | Please clarify; all these lines have spectacle blinds at close position
9 | Callout | 1 | Francis L | Tag as FC. Applies to all other similar tags.