## 051-A-PID-00026-001-RA-CS
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Callout | 1 | Francis L | Clarify requirement for level bridles.
2 | Call-out | 1 | MAK | Add REFRIGERATED
3 | Cloud+ | 1 | MAK | Delete
4 | Callout | 1 | Francis L | Indicate tag no. of instrument bubble.
5 | Callout | 1 | Francis L | Use PHC. Refer BMPS-A-50003.
6 | Callout | 1 | Francis L | Clarify functions of alarms.
7 | Callout | 1 | Francis L | Indicate type of split range. Refer BMPS-A-50003, sht 3. Tag the first valve to be acted on with suffix A. Use same sequential no. for the entire split range loop.