## 051-A-PID-00036-001-RA-CS
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Call-out | 1 | Abdul Rahim | Pls advise if this pump can be started from the control room
2 | Text Box | 1 | MAK | 051M0005A
3 | Text Box | 1 | MAK | General Comment to be applied to all P&IDs: As per BMPS-A8, Section 8.4.3, Drivers Tag Nos. e.g. Motors/Turbines shall always be inserted in all P&IDs and placed below the parent equipment no. e.g. Pump/Fan/Mixer/Cooler where possible. Motor FinFan tag nos. shall always be shown where applicable.
4 | Callout | 1 | Francis L | - Include AUTO - Clarify whether DCS "ON" is needed
5 | Callout | 1 | Francis L | Please de-clutter
6 | Cloud+ | 1 | MAK | Delete
7 | Callout | 1 | Francis L | - Clarify signal route of signal. - Clarify condition for permissive and add as Note. - Applicable to all other similar l oops.
8 | Callout | 1 | Francis L | froml
9 | Call-out | 1 | Abdul Rahim | Add tank number
10 | Call-out | 1 | MAK | Add REFRIGERATED
11 | Call-out | 1 | Abdul Rahim | Add tank capacity and dimention
12 | Callout | 1 | Francis L | Indicate the relevant valve.
13 | Callout | 1 | Francis L | Clarify whether this is required.
14 | Call-out | 1 | Abdul Rahim | Pls discuss where is the location of this vent
15 | Text Box | 1 | MAK | 051M0005B