## 051-A-PID-00038-001-RA-CS
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Text Box | 1 | MAK | 051M0007B
2 | Text Box | 1 | MAK | General Comment to be applied to all P&IDs: As per BMPS-A8, Section 8.4.3, Drivers Tag Nos. e.g. Motors/Turbines shall always be inserted in all P&IDs and placed below the parent equipment no. e.g. Pump/Fan/Mixer/Cooler where possible. Motor FinFan tag nos. shall always be shown where applicable.
3 | Text Box | 1 | MAK | 051M0007A
4 | Cloud+ | 1 | MAK | Delete
5 | Call-out | 1 | MAK | Add REFRIGERATED
6 | Text Box | 1 | Francis L | Refer to comments on sht 36