## 051-A-PID-00039-001-RA-CS
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Callout | 1 | Francis L | Clarify whether it can be installed on the side of vessel with bridle detail type stated.
2 | Call-out | 1 | Abdul Rahim | Delete
3 | Call-out | 1 | Abdul Rahim | does 100% means five fire pumps running at full load for 16 hours
4 | Callout | 1 | A Albalooshi | This is applicable to all P&ID's. EPC contractor shall take into considerations the following to reduce the vibration level: 1- Discuss with coupling manufacturer to reduce the vibration transmitted from the diesel engine. 2- Design the suction piping and layout of pumps (by providing adequate straight suction length. 10D) to reduce the vibration induced due to hydraulics. 3- Provide adequate vibration dampeners for diesel engine. 4- Design and provide adequate foundation.
5 | Callout | 1 | Francis L | Clarify whether transmitters and indications can be provided as well.
6 | Callout | 1 | Francis L | This note is relevant to horn.
7 | Call-out | 1 | Abdul Rahim | what kind of assurance there will be to protect against water leaks inside pumps area and will there be automatic pump out pumps to discharge water. We need to think carefully about this design we need one incident of leak and all pumps and engines will be under water
8 | Text Box | 1 | Mahdi Ali | THIS APPLICABLE FOR ALL THE PIDS. 1. TAG NUMBER FOR THE DRIVER FOR ROTATING EQUIPMENT SUCH AS PUMPS OR COMPRESSORS SHALL BE INSERTED ON ALL PIDS AS PER BMPS-A8 SECTION 8.4.3. 2. USE UPDATED LINE TYPE FOR FIELDBUS SIGNAL. 3. MAKE SURE THAT CORRECT OPC TYPE IS USED FOR UTILITIES AND PROCESS 4. EQUIPMENT TAG SHALL NOT CONTAIN SPACES.
9 | Call-out | 1 | Abdul Rahim | consider insertion of a blind
10 | Callout | 1 | A Albalooshi | Please advise if vertical drain sump pumps are provided in case of over flow.
11 | Call-out | 1 | Abdul Rahim | Pls advise if not divers require to go fore any cleaning
12 | Callout | 1 | Francis L | Clarify function
13 | Call-out | 1 | Abdul Rahim | is there any main fire water pressure transmitter connecting the control room
14 | Call-out | 1 | Abdul Rahim | Pls explain
15 | Text Box | 1 | Abdul Rahim | Since this area will be a confined space, what kind on protection there will be to protect operators from any fumes presence. i.e O2 continuous monitor.
16 | Callout | 1 | Francis L | Include - FIRE WATER PUMP
17 | Callout | 1 | Francis L | Clarify function.
18 | Text Box | 1 | Edgardo | Comments that would be generated and agreed upon during the Joint PID review between Bapco and TTSJV shall be incorporated in the applicable sheets of Unit 051 PID. This comment applies to all sheets of Unit 051 PID
19 | Call-out | 1 | Abdul Rahim | Bapco Marine Engineering Section needs to be full involved with respect to Fire pump engine
20 | Callout | 1 | Francis L | Common alarm shall be tagged as XA
21 | Call-out | 1 | Abdul Rahim | Add capacity in barrles
22 | Call-out | 1 | Abdul Rahim | discuss why horizontal installation
23 | Call-out | 1 | Abdul Rahim | Refrigerated
24 | Call-out | 1 | Abdul Rahim | why there is no valve
25 | Line | 1 | Abdul Rahim | Please provide flame arrestor
26 | Callout | 1 | Francis L | Tag flow sight as special piping equipment
27 | Call-out | 1 | Abdul Rahim | Reliability and maintainability to be discussed
28 | Text Box | 1 | Abdul Rahim | Where is the testing flow meter for the fire system
29 | Call-out | 1 | Abdul Rahim | Pls explain
30 | Text Box | 1 | Abdul Rahim | Comments on this sheet will apply to other similar sheets
31 | Callout | 1 | Francis L | Clarify function of ESD.
32 | Cloud+ | 1 | MAK | Use the correct Bapco document number.
33 | Call-out | 1 | Abdul Rahim | Change to meter