## 051-A-PID-00043-001-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Cloud+ | 1 | MAK | 051 - REFRIGERATED LPG C3/C4 STORAGE FACILITY AT WHARF
2 | Text Box | 1 | MAK | 051M0014A
3 | Text Box | 1 | MAK | 051M0014B
4 | Callout | 1 | Mahdi Ali | 61
5 | Callout | 1 | Francis L | Clarify function of LL
6 | Callout | 1 | Abdul Rahim | Does this mean specific Gravity
7 | Callout | 1 | Mahdi Ali | FIRST LINE SHALL BE P&ID ONLY. MOVE THE REST TO THE SECOND AND THIRD LINES
8 | Text Box | 1 | MAK | General Comment to be applied to all P&IDs: As per BMPS-A8, Section 8.4.3, Drivers Tag Nos. e.g. Motors/Turbines shall always be inserted in all P&IDs and placed below the parent equipment no. e.g. Pump/Fan/Mixer/Cooler where possible. Motor FinFan tag nos. shall always be shown where applicable.
9 | Text Box | 1 | Omran A | General comment: Remove Liquid Level from: LLL LLLL HLL HHLL
10 | Callout | 1 | Mahdi Ali | INCORRECT TAG FORMAT. SHALL BE 051D0900 AND 051D0920
11 | Callout | 1 | Francis L | Indicate location of this indicator
12 | Callout | 1 | Abdul Rahim | Is the size of this connection is suitable for air driven pump out pump if both electrical pumps are out of service
13 | Text Box | 1 | Newlito Diaz | line number ending is 9 to PID 051-A-PID-00044-001 to be corrected.
14 | Text Box | 1 | Newlito Diaz | line number last two digit is 32 to PID 051-A-PID-00045-001 to be corrected.
15 | Callout | 1 | Abdul Rahim | Pls add, Basin Capacity in barrels
16 | Callout | 1 | Francis L | Remove these level settings from drawing.
17 | Callout | 1 | Abdul Rahim | the design of the basin should cater for complete repair for the future
18 | Callout | 1 | Abdul Rahim | TTSJV to ensure that D 900/920 slop tanks at Sitra Tanks are adequate to receive the anticipated quantity of oily water