## 051-A-PID-00044-001-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Cloud+ | 1 | MAK | 051 - REFRIGERATED LPG C3/C4 STORAGE FACILITY AT WHARF
2 | Callout | 1 | Francis L | Clarify functions of these alarms.
3 | Callout | 1 | Francis L | Indicate which manual valve.
4 | Callout | 1 | Francis L | Low level
5 | Callout | 1 | Abdul Rahim | Pls add basin capacity
6 | Cloud+ | 1 | MAK | Remove from first line
7 | Callout | 1 | Abdul Rahim | The capacity of this pump is approx 570 BPH. Note the Minimum capacity are kept for both tanks at Sitra Tank 900/920 is 5000 barrels only, during raining day Sitra Tanks separator will be loaded. Please ensure the contaminated storm water can be adequately taken to with out overloading Sitra system.