## 051-A-PPN-00001-001-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Cloud+ | 1 | MAK | 051 - REFRIGERATED LPG C3/C4 STORAGE FACILITY AT WHARF
2 | Call-out | 1 | Ahmed Habib | 165SRR01 Satellite Rack Room
3 | Callout | 1 | David.Jimenez | E
4 | Text Box | 1 | Francis L | Ensure that paved access is provided from roadway to rack room entrance designated for moving equipment such as control cabinets in and out of the building.
5 | Call-out | 1 | Edgardo | For clarity, please include a table showing these tags and their general description; as an Example, Platform - N061PLF500; etc. This comment applies to all the tagged structures shown in this document
6 | Text Box | 1 | Abdul Rahim | I assume fire fighting equipment will be on another plot plan sheet
7 | Call-out | 1 | Edgardo | Include a Note to read "For Section Views, refer to Drawing 051-A-PPN-00001-002."
8 | Call-out | 1 | Mohamed Aldoseri | Paved area shall be provided for equipment loading access
9 | Call-out | 1 | Edgardo | Please clarify HPR; this is not included in the Legend
10 | Call-out | 1 | Edgardo | Please clarify if the segregation between the two trains of the Refrigeration Facilities will provide safe distance to carry out T&I work on one train while the other train is in operation
11 | Call-out | 1 | Edgardo | Please clarify if these are overhead pipe racks; If yes, please indicate the location of the required Height Protection Barriers
12 | Call-out | 1 | Edgardo | Please clarify if this is part of platform N051PLF200; In Section C-C, the clearance of this platform from grade is 3 m; Please ensure that adequate clearance is provided for access to equipment during maintenance work
13 | Call-out | 1 | Edgardo | Please clarify the "At Grade " location; These pumps are installed inside the tank
14 | Call-out | 1 | Edgardo | Please clarify the accessibility of these equipment during maintenance work
15 | Call-out | 1 | Edgardo | Please clarify this Section F-F in N051PR100; In 051-A-PPN-00001-002, Section F-F is only for piperacks N051PR400, 500 and 600
16 | Call-out | 1 | Edgardo | Please clarify this symbol; this is not shown on the Legends; The car park shall also be paved
17 | Call-out | 1 | Edgardo | Please confirm the provision of these sanitary pumps; refer to Owner's comments in the 051 PID review
18 | Call-out | 1 | Edgardo | Please include both the building name and building number; Rectify the building number also as follows: This is Wharf C3/C4 Substation 051SSTW01
19 | Call-out | 1 | Edgardo | Please provide paved service road to access the HVAC equipment during maintenance work
20 | Call-out | 1 | Edgardo | Provide service road to this basin for access of the vacuum trucks and service equipment during maintenance work on this basin
21 | Text Box | 1 | AliRedha Malalla | Reference to Maintenance Consideration Report para 5.2.1; overhead crane shall be considered for both compressor trains.
22 | Text Box | 1 | MAK | S
23 | Text Box | 1 | MAK | S
24 | Text Box | 1 | MAK | S
25 | Text Box | 1 | MAK | S
26 | Text Box | 1 | MAK | S
27 | Text Box | 1 | MAK | S
28 | Callout | 1 | Chandrahasan D | See Comments on Coordinates in General Notes. (typical for all boundary coordinates)
29 | Text Box | 1 | Chandrahasan D | SHOW AREAS FOR -CIRCUIT BUS STOP, SMOKING SHELTER AND CAR PARKS FOR COMPANY, CONTRACTOR PERSONNEL AND VISITORS - LAYDOWN AREA FOR T&I - TOILET AND PRAYER ROOM AMENITIES FOR CONTRACTOR WORKFORCE AND VISITORS -- Exclusion zone for other future construction in the vicinity
30 | Callout | 1 | A Albalooshi | Spacing between tanks shall meet NFPA 30 requirements
31 | Callout | 1 | A Albalooshi | Spacing between tanks shall meet NFPA 30 requirements
32 | Call-out | 1 | Edgardo | Suggest to use text which is more descriptive; For example: At Piperack N051PR100
33 | Callout | 1 | Abdul Rahim | the access should suitable for a crane to remove submersible pumps from tank
34 | Call-out | 1 | Mohamed Aldoseri | This area shall be paved
35 | Call-out | 1 | Edgardo | This area should include the parking space for the delivery truck during unloading liquid nitrogen
36 | Callout | 1 | Chandrahasan D | This coordinates and elevation apply to Sitra Tank farm only and Not for Wharf area. Wharf area use UTM coordinates and NSD.
37 | Cloud+ | 1 | MAK | Use short description C3/C4 AT WHARF