## 056-A-PID-00003-001-R5A
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Text Box | 1 | Omran A | ON
2 | Typewritten Text | 1 | Nabeel | Where is this going?
3 | Call-out | 1 | Edgardo | Please indicate size of reducers
4 | Typewritten Text | 1 | Nabeel | use the word "Trips"
5 | Text Box | 1 | Mahdi Ali | Add the above note below the drawing number as was originally provided by Bapco. Do not remove this note from all the PID provided by Bapco.
6 | Text Box | 1 | Mahdi Ali | THIS DRAWING IS CONVERTED FROM BRA175621-001
7 | Call-out | 1 | Edgardo | This line need not be drawn with heavy line as it is already clouded to show it is a new line
8 | Call-out | 1 | Abdul Rahim | can not find sheet 6
9 | Call-out | 1 | Ali Abbas | General comments for all P&IDs effected by PLC to DCS upgrades: All the P&IDs symbology to be updated to reflect DCS control instead of PLC control.
10 | Call-out | 1 | Abdul Rahim | this comment is not applicale to this P&ID
11 | Text Box | 1 | Francis L | All existing instrumentation that are associated with the DCS upgrade shall be redrawn to reflect DCS symbology.
12 | Call-out | 1 | Edgardo | Please indicate the size of valve
13 | Call-out | 1 | Abdul Rahim | can not find note 9?
14 | Text Box | 1 | MAK | 056M5606
15 | Call-out | 1 | Abdul Rahim | add
16 | Call-out | 1 | Abdul Rahim | in addition, override switch to enable loading if MOV status in error
17 | Call-out | 1 | Edgardo | include also the low point drains
18 | Call-out | 1 | Ali Abbas | Need to clarify and more details about ESD
19 | Call-out | 1 | Edgardo | Please minimize the long line breaks as much as possible
20 | Call-out | 1 | Abdul Rahim | closed against pump
21 | Call-out | 1 | Ali Abbas | delete suffix A
22 | Call-out | 1 | Abdul Rahim | explain this note, irrelevant
23 | Call-out | 1 | Abdul Rahim | tripped against high pressure
24 | Line | 1 | Abdul Rahim
25 | Typewritten Text | 1 | Nabeel | Please confirm the discharge pressure value!
26 | Call-out | 1 | MAK | General Comment to be applied to all P&IDs: As per BMPS-A8, Section 8.4.3, Drivers Tag Nos. e.g. Motors/Turbines shall always be inserted in all P&IDs and placed below the parent equipment no. e.g. Pump/Mixer/Cooler where possible.
27 | Call-out | 1 | Abdul Rahim | Explain why there is no 16" valve and how pig launcher will be installed