## 056-A-PID-00004-001-R2A
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Call-out | 1 | Abdul Rahim | in addition, override switch to be installed to enable loading if MOV status in error
2 | Call-out | 1 | Abdul Rahim | suction
3 | Text Box | 1 | Francis L | Due to upgrade of PLC to DCS for Sitra Tanks and Wharf, update instrument symbols from PLC to DCS.
4 | Text Box | 1 | Abdul Rahim | White Diesel Suction
5 | Call-out | 1 | Edgardo | Please clarify the relationship of the tie-in schedule with the T&I of the refinery units, noting that these tie-ins are at Sitra Tank Farm. This comment applies to all sheets where there is a note regarding expected date for tie-in execution
6 | Text Box | 1 | Mahdi Ali | Add the above note below the drawing number as was originally provided by Bapco. Do not remove this note from all the PID provided by Bapco.
7 | Text Box | 1 | Mahdi Ali | THIS DRAWING IS CONVERTED FROM BRA-179684-001
8 | Call-out | 1 | Abdul Rahim | Suction
9 | Call-out | 1 | Edgardo | As previously discussed during PID review, size of drain valves for new lines shall at least be 1 1/2" to allow connections of hose for draining and for shorter draining time. The pipes at the Tank Farm are longer and pipe contents are more compared to those at process units. The size of the vent valve is acceptable. This comment applies to all PID sheets in this unit
10 | Callout | 1 | Francis L | Indicate instrument air symbology