## 056-A-PID-00010-002-R4A
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Call-out | 1 | Edgardo | The size of drain valve shall be minimum 1 1/2" per BMPS-L-144014
2 | Call-out | 1 | Abdul Rahim | General Item Any tie-in on tank filling and suction lines can be done during planned window. However, if a tie-in is through tank shell then the tank needs to be taken out of service
3 | Call-out | 1 | Abdul Rahim | for
4 | Call-out | 1 | Edgardo | These 2" valves shall be shown with blind, instead of plugs
5 | Call-out | 1 | Edgardo | Please rectify line number
6 | Call-out | 1 | Edgardo | Please change size to 16"
7 | Call-out | 1 | Abdul Rahim | correct this statement, Owner shall accept using tank manway as alternative method for tie-in point in tank if proven satisfactory from design point of view and if permanent tank nozzle will affect project schedule.
8 | Text Box | 1 | Mahdi Ali | THIS DRAWING IS CONVERTED FROM BRA080051-002
9 | Call-out | 1 | Abdul Rahim | internal transfer
10 | Text Box | 1 | Mahdi Ali | Add the above note below the drawing number as was originally provided by Bapco. Do not remove this note from all the PID provided by Bapco.
11 | Call-out | 1 | Abdul Rahim | root valves on tank
12 | Call-out | 1 | Abdul Rahim | this note is deleted
13 | Text Box | 1 | Edgardo | Refer to comment on 056-A-PID-00004-001 regarding size of drain valves on the new lines
14 | Call-out | 1 | Abdul Rahim | line