## 056-A-PID-00015-001-R6A
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Text Box | 1 | Mahdi Ali | Add the above note below the drawing number as was originally provided by Bapco. Do not remove this note from all the PID provided by Bapco.
2 | Callout | 1 | Francis L | Amend to DCS bubble. Applies to all other similar and relevant PLC tags.
3 | Call-out | 1 | Abdul Rahim | General comment Improve on all label name ie from where /to where and line number if applicable ie new diesel transfer line to Sitra is # 540
4 | Call-out | 1 | Abdul Rahim | General comment Some of these installation are removed to be checked during site survey
5 | Callout | 1 | Francis L | Indicate as electronic signal lines ie. dashed lines. Applies to all other similar and relevant signal lines.
6 | Callout | 1 | Francis L | Indicate description/product of tank for this and all other tanks.
7 | Call-out | 1 | Edgardo | Please change drain size to 2"
8 | Call-out | 1 | Edgardo | Please include a Note that this valve should be verified at site if already existing
9 | Call-out | 1 | Edgardo | Please minimize the very long line break
10 | Call-out | 1 | Edgardo | The 4" stubs is no longer required, since the existing fill line has already a 4" stub for initial filling
11 | Call-out | 1 | Edgardo | The drain valve shall be provided with blind instead of plug
12 | Text Box | 1 | Mahdi Ali | THIS DRAWING IS CONVERTED FROM BRA080057-001