## 056-A-PID-00015-002-R6A
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Call-out | 1 | Abdul Rahim | General comment. Please standardize some tanks with no product name.
2 | Text Box | 1 | Mahdi Ali | THIS DRAWING IS CONVERTED FROM BRA080057-002
3 | Call-out | 1 | Abdul Rahim | This is general item check at site, this is now modified through the shell
4 | Text Box | 1 | Edgardo | NC
5 | Call-out | 1 | Abdul Rahim | is this suction
6 | Call-out | 1 | Edgardo | Please confirm this tie-in.
7 | Call-out | 1 | Abdul Rahim | via # 540 line
8 | Text Box | 1 | Mahdi Ali | Add the above note below the drawing number as was originally provided by Bapco. Do not remove this note from all the PID provided by Bapco.
9 | Call-out | 1 | Abdul Rahim | Do not use existing Enraf temperature for heating coil. Tank level will remain as is.
10 | Call-out | 1 | Abdul Rahim | Change all diesel tank product to 10 ppm diesel
11 | Call-out | 1 | Edgardo | Show NC on the bypass valve
12 | Call-out | 1 | Abdul Rahim | please discuss, looks complicated. We need 4" valves on filling and suction line close to the tank. For initial filling a 4" cargo hose will be connected to the water draw valve from either filling or suction lines.
13 | Call-out | 1 | Abdul Rahim | add : the number of transfer line. also standardize either call it diesel or 10 ppm diesel
14 | Call-out | 1 | Abdul Rahim | This is a general item. This needs to be confirmed at site. In addition check the adequacy of existing vent for post BMP