## 056-A-PID-00015-007-R6A
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Call-out | 1 | Edgardo | This drain valve can be removed
2 | Call-out | 1 | Edgardo | Please change size to 4" as this will be used for initial filling of tank
3 | Call-out | 1 | Abdul Rahim | confirm requirement
4 | Text Box | 1 | Mahdi Ali | Add the above note below the drawing number as was originally provided by Bapco. Do not remove this note from all the PID provided by Bapco.
5 | Call-out | 1 | Abdul Rahim | Add size
6 | Call-out | 1 | Edgardo | Please provide vent and drain valve
7 | Callout | 1 | Francis L | Indicate as electronic signal (dashed line).
8 | Text Box | 1 | Mahdi Ali | 056-A-PID-00015-007 IS AN EXISTING SHEET. THIS DRAWING SHALL BE SHEET NO. 8 OR 9. ALL THE OPCS SHALL CHANGE ACCORDINGLY.
9 | Call-out | 1 | Abdul Rahim | to be removed
10 | Text Box | 1 | Mahdi Ali | THIS DRAWING IS CONVERTED FROM BRA080057-001