## 056-A-PID-00020-001-R4A
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Text Box | 1 | Mahdi Ali | THIS DRAWING IS CONVERTED FROM BRA080064-001
2 | Call-out | 1 | Edgardo | Please provide this line with vent and drain valves
3 | Callout | 1 | Francis L | Indicate as "0621".
4 | Callout | 1 | Francis L | Clarify and indicate with better clarity of function of the two signals connected to one indicator.
5 | Text Box | 1 | Francis L | Clarify whether these instruments are to be demolished.
6 | Text Box | 1 | Mahdi Ali | Add the above note below the drawing number as was originally provided by Bapco. Do not remove this note from all the PID provided by Bapco.
7 | Callout | 1 | Francis L | Indicate as DCS tag - FQC.
8 | Callout | 1 | Francis L | Clarify function of two transmitter signals connected to totaliser controller. May need to indicate in better detail/clarity.
9 | Call-out | 1 | Edgardo | Provide connection of this Line P5613 to S/L # 51 for the required line flushing
10 | Callout | 1 | Francis L | Indicate as pneumatic signal.
11 | Callout | 1 | Francis L | Clarify whether these instruments and any association on PID 00023 are to be demolished.
12 | Call-out | 1 | Edgardo | Please indicate size of valve
13 | Callout | 1 | Francis L | Indicate Wharf plant number at top right of symbol - "061".
14 | Callout | 1 | Francis L | Clarify whether these instruments are to be demolished as well.
15 | Callout | 1 | Francis L | Remove boxes around tags inside bubble.
16 | Call-out | 1 | Edgardo | These lines belong to Unit 061 and hence, the line numbers should start with 061 instead of 056