## 056-A-PID-00021-001-R4A
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Callout | 1 | Francis L | Remove arrow at this end.
2 | Callout | 1 | Francis L | Indicate as "FC"
3 | Call-out | 1 | Edgardo | Please provide this line with vent and drain valves
4 | Text Box | 1 | Mahdi Ali | THIS DRAWING IS CONVERTED FROM BRA080065-001
5 | Callout | 1 | Francis L | Indicate as pneumatic signal.
6 | Callout | 1 | Francis L | Indicate as pneumatic signal.
7 | Text Box | 1 | Mahdi Ali | Add the above note below the drawing number as was originally provided by Bapco. Do not remove this note from all the PID provided by Bapco.
8 | Callout | 1 | Francis L | Clarify and indicate more symbology detail as per BMPS-50003, for motor status feedback, motor control, etc, which will be configured on new DCS. Applies to all other similar motors/tags.