## 056-G-DAT-50003-001-RB
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Text Box | 1 | Mahdi Ali | THIS DATASHEET TEMPLATE WAS REVISED AND WILL BE ISSUED WITH THE HOMOGENIZATION PROCEDURE. IN THE NEXT REVISION, THE REVISED TEMPLATE AND COVER PAGE SHALL BE USED.
2 | Callout | 2 | Mahdi Ali | 056 - SITRA TANK FARM
3 | Text Box | 2 | A Albalooshi | The information provided for the driver starting method of the pumps is not applicable (Closed/Open – valve (unloaded) start)), It shall be corrected as DOL or VFD starting method as per detail design. Please provide the basis/ philosophy of providing this requirement on the driver starting method. A general note shall be added as follows "Motors shall be designed to suite the driver online starting method as per BMPS-P19 clause 5.4 and BMPS-P18 clause 5.4.". The (Closed/Open – valve (unloaded) start)) shall be moved in the relevant field in the data sheet.
4 | Call-out | 2 | Mohamed Aldoseri | Area classification shall be confirmed after the final HAC drawing, considering API 500 as indicated in BMPS-P2- Typical to all pumps/motors in existing areas.