## 058-A-PID-00001-010-R7A
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Call-out | 1 | Edgardo | Please show the B/L for this line, which is coming from Unit 933
2 | Callout | 1 | Julio.Aguilar | Review and confirm the symbol of this instrument line with the BMPS-A50003
3 | Callout | 1 | A Albalooshi | Bapco will review and advise the opportunity of the tie -in execution. EPC contractor shall provide the company S/D sequence without jeopardizing the operation and safety of the units.
4 | Text Box | 1 | Julio.Aguilar | As per BMPS-A8 all valve sizes shall be noted next to the valves where different from line size. In this PID the valve sizes are shown despite the line size is same. E.g
5 | Cloud+ | 1 | Julio.Aguilar | Clarify location of this vent.
6 | Call-out | 1 | Ali Hasan | Add drain upstream the blind
7 | Call-out | 1 | Ali Hasan | Please add a note stating that this line is NNF for consistency with the note in 1HRU P&ID.
8 | Cloud+ | 1 | MAK | REFINERY GAS SYSTEM