## 061-A-PID-00014-001-R4A
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Callout | 1 | Francis L | Indicate as dashed line
2 | Call-out | 1 | Mahdi Ali | RETAIN EXISTING INFORMATION. THE '62756 AND EN0815 SHALL BE INSERTED IN BAPCO REVISION BOX FOR THE FINAL HANDOVER. THIS NOTE APPLIED TO ALL BAPCO EXISTING DRAWINGS
3 | Callout | 1 | Francis L | Indicate connection for pilot signal
4 | Callout | 1 | Francis L | Update to DCS tag. Applies to all other such tags.
5 | Callout | 1 | Francis L | Amend to indicate electronic signal (dashed line). Applies to all other similar and relevant signals.
6 | Callout | 1 | Francis L | Correct signal type to electronic (dashed line).
7 | Typewritten Text | 1 | Nabeel | Insert description of the Tanks
8 | Text Box | 1 | Mahdi Ali | BAPCO LEGACY DRAWING NO. BRA080084 SHEET 1
9 | Text Box | 1 | Mahdi Ali | ADD THE ABOVE NOTE BELOW THE DRAWING NUMBER AS WAS ORIGINALLY PROVIDED BY BAPCO. DO NOT REMOVE THIS NOTE FROM ALL THE PID PROVIDED BY BAPCO.