## 061-S-DAT-50012-001-RA-CS
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Callout | Page 2 | Abdul Rahim | same as 061LA 6131
2 | Callout | Page 2 | Chandrahasan D | <add> Design Basic wind speed for operating and idle conditions
3 | Call-out | Page 3 | Mohamed Aldoseri | Refer to comments in (061-S-DAT-50002-001)
4 | Callout | Page 3 | Chandrahasan D | <add> Minimum vessel size in addition to the maximum vessel size
5 | Text Box | Page 4 | Chandrahasan D | General: The minimum value of M in the existing wharf operations is 3m The value B in existing T wharf is more than 6m This spacing J need to be checked with pile row spacing to avoid interference with existing structures The O range value is very narrow and needs to be checked with vessel size range
6 | Callout | Page 4 | Chandrahasan D | counterweight movement envelope to be provided by vendor and EPC contractor to check and ensure that no interference with existing structure/services and personnel movement
7 | Text Box | Page 4 | Chandrahasan D | General: Missing Dimensions F,G,H &I to be provided by vendor and to be verified by EPC contractor?? Vendor to provide Loading information for design of Structures/foundation