## 079-A-PID-00003-001-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Text Box | 1 | Francis L | A separate LI could be considered for: - replacing the high and low alarms on LC0003 - tripping the flow controllers on HH level. This requirement may be studied during HAZOP.
2 | Callout | 1 | Francis L | Amend to "condition"
3 | Callout | 1 | Francis L | Clarify whether this equipment is on sht 6 as unit no. is 015.
4 | Callout | 1 | Francis L | controllers
5 | Callout | 1 | Francis L | Indicate as "Low level will reset ...."
6 | Callout | 1 | Francis L | Indicate as "Low low level"
7 | Callout | 1 | Francis L | Indicate Hold 9 point here.
8 | Callout | 1 | Francis L | Indicate MAG against the bubble, for magnetic type level gauge.
9 | Callout | 1 | Francis L | Indicate SP for this signal here
10 | Callout | 1 | Francis L | Indicate type of bridle for drain, etc.
11 | Callout | 1 | Francis L | Is there a requirement for this to be readable at a specific location? If so, insert a note.
12 | Call-out | 1 | Ali Hasan | MIN can be shown as one line up to the check valve flange instead of two sections. This comment is also applicable to other streams with the same arrangement.
13 | Callout | 1 | Francis L | Note that sequential numbers of ESD tags are of 8000 series. ESD output action should not be used to close a valve via DCS. Clarify as this ESD has three LIs on DCS but one transmitter. Provide a sequential number for this tag.
14 | Call-out | 1 | Ranjit | Please clarify the sizing criteria. If any other case than fire, we will need two valves.
15 | Text Box | 1 | Francis L | Provide instrumentation as per Owner standard arrangement.
16 | Call-out | 1 | Ranjit | Provide separate LI for alarm. The LI used for control cannot be used for Alarms
17 | Callout | 1 | Francis L | Remove the alarms as these will be indicated on the associated Cause & Effect diagram.
18 | Call-out | 1 | Ali Hasan | The PFD 079-A-PFD-00001-001 to be updated to reflect 079V0002 and vessel's inlet/outlet piping arrangement as shown in the P&ID.
19 | Callout | 1 | Francis L | This note refers to start permissive for pumps in 079U0001. However, signal is connected to pumps 0002A/B. Please clarify.
20 | Call-out | 1 | Ali Hasan | Tripping of the pumps on low-low level is throught ESD signal whereas the permissive to re-start the pumps is by DCS as explained in Note 2.
21 | Callout | 1 | Francis L | Vessel level alarm set points should not be indicated on P&IDs.