## 079-A-PID-00004-001-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Text Box | 1 | MAK | 079M0001A
2 | Callout | 1 | Francis L | Clarify function of this alarm.
3 | Callout | 1 | Francis L | Clarify number of pumps, as only one pump is shown in 079V0001
4 | Call-out | 1 | MAK | General Comment to be applied to all P&IDs: As per BMPS-A8, Section 8.4.3, Drivers Tag Nos. e.g. Motors/Turbines shall always be inserted in all P&IDs and placed below the parent equipment no. e.g. Pump/Fan/Mixer/Cooler where possible. Motor FinFan tag nos. shall always be shown where applicable.
5 | Callout | 1 | Francis L | IN
6 | Callout | 1 | Francis L | Indicate GWR against tag if guided wave radar type LIT is used.
7 | Callout | 1 | Francis L | ON
8 | Callout | 1 | A Albalooshi | Please confirm the suction pressure
9 | Call-out | 1 | Edgardo | Please indicate size of valve
10 | Callout | 1 | A Albalooshi | Please indicate the size
11 | Call-out | 1 | Ranjit | Provide steam out connection
12 | Call-out | 1 | Ranjit | Provide warehouse spare pump as per the philosophy adopted for other underground vessels
13 | Callout | 1 | Francis L | Remove from P&ID
14 | Call-out | 1 | Ranjit | The vent can have foul smell. Provide carbon filters. Alternately, can this be nitrogen urged with connection to flare. This approach will be similar to other underground vessels