## 079-C-DAT-00002-001-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Call-out | 2 | Ahmed Bucheeri | To be fully radiographed due to PWHT
2 | Call-out | 3 | Ahmed Bucheeri | Internal coating is required against internal corrosion, coating system to be selected basis the service contents and design temperature
3 | Callout | 5 | A Albalooshi | Line sizes in the P&IDs are preliminary and this shall be finalized along with Hydraulic calculations during detailed engineering stage of the EPC “The sizes are minimum in the P&IDs”. This document shall be updated after unfreezing the “HOLD” from the P&IDs.
4 | Callout | 5 | A Albalooshi | The size has been revised as per revised markup P&ID from 3" to 4".