## 081-A-PID-00001-003-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Call-out | 1 | Ali Hasan | add: and stop on low level.
2 | Call-out | 1 | Ali Hasan | add: both pumps.
3 | Text Box | 1 | Ahmed Habib | General Note: "D" suffix shall be used in E.M. CLOSE. Refer to latest SPI Database Creation Guidlines.
4 | Call-out | 1 | Edgardo | Please clarify who and when the HOLDS items will be cleared
5 | Call-out | 1 | Ali Hasan | provide local/remote switch to allow MOV opening from DCS
6 | Call-out | 1 | Ali Hasan | Provide OPEN signal
7 | Call-out | 1 | Ali Hasan | Refer to the ultrasonic representation in sheet 081-A-PID-00001-001. The FIT1012 representation may change based on the ultrasonic details provided by the vendor.
8 | Text Box | 1 | Mahdi Ali | Tag number for the driver for pumps shall be inserted on all PIDs as per BMPS-A8 section 8.4.3
9 | Call-out | 1 | Ali Hasan | The HH and LL level actions is related to Note 12. Change Note 6 to 12.
10 | Call-out | 1 | Ali Hasan | The rational for closing the MOV in case of high temperature to be discussed during the IBD P&ID review session.
11 | Call-out | 1 | Ali Hasan | The requirement for local panel for MOV and pumps start/stop to be discussed in the IBD P&ID review session.