## 082-G-DAT-00002-001-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Text Box | 1 | Isamu | This cover page differs from the ones for other pumps in the same transmittal. Please provide uniform cover page
2 | Text Box | 1 | Mahdi Ali | THIS DATASHEET TEMPLATE WAS REVISED AND WILL BE ISSUED WITH THE HOMOGENIZATION PROCEDURE. IN THE NEXT REVISION, THE REVISED TEMPLATE AND COVER PAGE SHALL BE USED.
3 | Text Box | 5 | Isamu | Please comply with FEED DS requirement for witnessed inspection and test. Changing to observed is rejected without Owner prior approval on selected test and selected pump on case by case basis. There is no "Observe" level of inspection in the ITB (BMPS-G-50309) and "witness" must be retained on the data sheet in line with the definition of the ITP. Also Refer to BMPS-B11 / BMPS-G1 / API 610 parag 3.64 and 3.38 for definitions of witness.