## 082-S-GAD-00001-001-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Text Box | [1] Layout1 | Ebrahim | PLEASE REFER TO OUR GENERAL COMMENTS ON TRANSMITTAL BMP-ROC-TRI-00199
2 | Call-out | [1] Layout1 | Edgardo | Please indicate the drawing numbers for the continuation of these lines
3 | Call-out | [1] Layout1 | Ali Hasan | The vents from the Manhole are generally located away from the process or working area. Please ensure the minimum safe distance is provided for these vents according to the project specification.
4 | Text Box | [1] Layout1 | Robert.Kawitzki | Show section
5 |  | [1] Layout1 | AutoCAD SHX Text | N
6 | Call-out | [1] Layout1 | Ali Hasan | Please provide paved surface and drainage instead of soakpit.
7 | Text Box | [1] Layout1 | Robert.Kawitzki | Confirm runoff direction
8 | Text Box | [1] Layout1 | Chandrahasan D | Clarify whether this is a Composite U/g network drawing (which shows all u/g utilities) OR not. Also, the foundation outlines shown are indicative , since the design can be finalised after soil investigation report.
9 | Call-out | [1] Layout1 | Edgardo | The presentation of the drawing extents / limits seems confusing. There is a continuation drawing shown (930-S-GAD-00001-008) yet there are also lines/facilities outside the drawing extents
10 | Callout | [1] Layout1 | Robert.Kawitzki | Show northings and eastings for all matchlines
11 | Call-out | [1] Layout1 | Edgardo | Please clarify what is SOAKAPIT and what is its purpose;
12 | Call-out | [1] Layout1 | Edgardo | SWS is not defined in this drawing
13 | Text Box | [1] Layout1 | AliRedha Malalla | Please ensure sufficient clearance in all directions between U/G service and pumps' foundation.
14 | Call-out | [1] Layout1 | Edgardo | Indicate the drawing number of the continuation of these lines
15 | Callout | [1] Layout1 | Chandrahasan D | Suggested to have common Abbreviation & Legend drawing for BMP and to be used by all operating centres.
16 | Call-out | [1] Layout1 | Edgardo | The drawing title is not consistent with the drawing contents, which also includes the U/G network for Unit 081 as well as the paving plans. These should be shown in different drawings
17 |  | [1] Layout1 | AutoCAD SHX Text | PIPEWAY
18 |  | [1] Layout1 | AutoCAD SHX Text | The present document or drawing is property of TECHNIP ITALY S.p.A. and shall not, under any circumstances, be totally or partially, directly or indirectly, transferred, reproduced, copied, disclosed or used, without its prior written consent, for any purpose and in any way other than that for which it is specifically furnished or outside the extent of the agreed upon right of use.
19 | Call-out | [1] Layout1 | Edgardo | Please change to Refinery South Flare
20 |  | [1] Layout1 | AutoCAD SHX Text | 81V8102
21 | Callout | [1] Layout1 | Chandrahasan D | Suggested to have one civil works Note drawing for BMP and to be used for all operating centres.
22 | Call-out | [1] Layout1 | Ali Hasan | Please ensure access to 082U0001 is provided through paved walkway.
23 |  | [1] Layout1 | AutoCAD SHX Text | 77V7740
24 | Call-out | [1] Layout1 | Edgardo | In the legend, the phrase "ECT W= H=" is shown but not in this trench ; this comment also applies to the Instrument trench
25 |  | [1] Layout1 | AutoCAD SHX Text | 81V8101
26 |  | [1] Layout1 | AutoCAD SHX Text | s
27 | Call-out | [1] Layout1 | Ali Hasan | Please refer to our comments on LSDP flare revamp PFD. The equipment number for the new vessel and pumps shall follow the existing equipment numbering system. The BMP numbering/tagging shall not be used for the revamp units/equipment.
28 | Callout | [1] Layout1 | Chandrahasan D | REFINERY
29 |  | [1] Layout1 | AutoCAD SHX Text | VENT STACK
30 | Callout | [1] Layout1 | Chandrahasan D | Drawing titles to be in accordance with BMPS-A8 section 6.3.2
31 | Call-out | [1] Layout1 | Edgardo | Please clarify SSR; Please use the designated unit name
32 | Callout | [1] Layout1 | Robert.Kawitzki | UG pipes shall not run under concrete slabs
33 | Call-out | [1] Layout1 | Edgardo | Drawing is for Unit 082 but drawing contents include those for Units 081 and 933
34 | Call-out | [1] Layout1 | Mohamed Aldoseri | Provide reference sectional drawing for cross over area between electrical/instrument cable trenches-Typical to all underground cable trenches
35 |  | [1] Layout1 | AutoCAD SHX Text | LSDP
36 | Callout | [1] Layout1 | Chandrahasan D | Verify the paving types to be shown in this drawing, if to be covered in separate drawing. Note that the legend does include paving types shown here.
37 | Text Box | [1] Layout1 | MAK | General Comment: The latest drawing borders have been submitted to JV Directorate on April 2018. Use the latest drawing borders that are part of the Homogenisation Procedure.
38 | Callout | [1] Layout1 | Mahdi Ali | CHANGE MATERIAL CLASS TO 'A'
39 | Call-out | [1] Layout1 | Edgardo | In the Plot Plan, this is shown as corridor for sanitary sewer, This drawing, however, shows the CSS, OWS and SWS. Please rectify the inconsistencies between the two drawings
40 | Callout | [1] Layout1 | Chandrahasan D | Use Separate Legend each u/g network
41 |  | [1] Layout1 | AutoCAD SHX Text | FLARE
42 |  | [1] Layout1 | AutoCAD SHX Text | s
43 | Call-out | [1] Layout1 | Edgardo | Please include in the legends / symbols these type of paving
44 | Cloud+ | [1] Layout1 | MAK | 082 - REFINERY SOUTH FLARE
45 | Callout | [1] Layout1 | Chandrahasan D | <add after corresponding to> UTM ZONE 39 COORDINATES â€“ AIN AL ABD DATUM <and before N=2887...>
46 | Cloud+ | [1] Layout1 | MAK | Fill in E.X. and P.N. nos.
47 | Callout | [1] Layout1 | Robert.Kawitzki | Show FGL at low point