## 180-A-PID-00001-001-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Text Box | 1 | MAK | 180M0001A
2 | Text Box | 1 | MAK | 180M0001B
3 | Callout | 1 | Bernard.Grace | Define access criteria for truck. Ideally include a plan identifying location for truck on this drawing?
4 | Text Box | 1 | MAK | General Comment to be applied to all P&IDs: As per BMPS-A8, Section 8.4.3, Drivers Tag Nos. e.g. Motors/Turbines shall always be inserted in all P&IDs and placed below the parent equipment no. e.g. Pump/Fan/Mixer/Cooler where possible. Motor FinFan tag nos. shall always be shown where applicable.
5 | Text Box | 1 | A Albalooshi | General comment: All applicable comments generated and agreed upon during the Joint PID Review between ROC and Owner shall be incorporated in the next update of the respective documents.
6 | Text Box | 1 | Omran A | General Comment: For consistency with Pump A, please keep PUMP B STOP and START suffix similar to Pump A.
7 | Cloud+ | 1 | MAK | L-144014
8 | Call-out | 1 | Edgardo | Please confirm the stream name and source, the basin is the Operation Building sanitary Basin but the stream is from Maintenance Workshop
9 | Callout | 1 | Bernard.Grace | provide minimum dimension
10 | Cloud+ | 1 | MAK | REFINERY SOUTH CONTROL BUILDING
11 | Cloud+ | 1 | MAK | Remove if from first line
12 | Callout | 1 | Bernard.Grace | The basin appears to be a concrete tank
13 | Callout | 1 | A Albalooshi | the sanitary septic tanks and pumps will be under Unit 382. The Common Alarm signal to DCS at the Utilities Control Room shall be retained
14 | Cloud+ | 1 | MAK | UNIT 180
15 | Callout | 1 | Bernard.Grace | What about perimeter fence to protect personnel moving around this area?