## 372-A-PFD-54001-001-RB-CS
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Text Box | 1 | BD Mori | The PFDs of unit 372 and newly created unit 370 shall be segregated and also stream data shall be segregated . After segregation, new PFD numbers shall be assigned.
2 | Cloud+ | 1 | Julio.Aguilar | Ensure that the differential pressure value is consistent with the new data sheet for the pump 372P3732A/B
3 | Call-out | 1 | Hasan Al Noaimi | Should read FED to Cooling Water Tower CWT
4 | Call-out | 1 | Hasan Al Noaimi | Refinery South Flare
5 | Callout | 1 | Julio.Aguilar | Revise equipment number as per last approved by the project
6 | Callout | 1 | Ebrahim.Deyab | Remove this number, already mentioned above unit 375
7 | Text Box | 1 | Mahdi Ali | Incorrect Off-page connectors. Follow the homogenization procedure
8 | Text Box | 1 | Julio.Aguilar | Drafting shall be as per BMPS-A8. Show Main, Secondary and Minor lines properly.
9 | Callout | 1 | Julio.Aguilar | Reword; FED WATER MAKE UP TO SECONDARY CWT BASIN
10 | Text Box | 1 | Mahdi Ali | Use the latest border that is part of the Homogenization procedure
11 | Callout | 1 | Julio.Aguilar | Reword; FED WATER MAKE UP TO MAIN CWT BASIN
12 | Callout | 1 | Julio.Aguilar | Add stream number