## 372-A-PFD-54001-010-RA-CS
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Text Box | 1 | MAK | General Comment: Follow the equipment nos. that have been sent officially through Project Mailbox.
2 | Callout | 1 | Salman Jaffer | This stream should go to 098-A-0001 and 099-A-0001 (sheet 3 of each)
3 | Text Box | 1 | MAK | A1
4 | Call-out | 1 | MAK | 17
5 | Callout | 1 | Julio.Aguilar | This line to be splitted in two to provide demin water to 099 unit.
6 | Text Box | 1 | MAK | Use the latest PFD border and off-page connectors that are part of the Homogenization Procedure. SOC shall coordinate with TTSJV.
7 | Text Box | 1 | Julio.Aguilar | Pumps 372P3740C to be reinstated in the PFD as they are feed pumps to the Hotwells -existing HP Boilers. They are critical pumps recommended to be included in the FEED Hazop and for critical pumps the philosophy mentioned is N+2; 1 pump in operation, one pump in stand-by and one pump in spare. See Process basis of design for sparing philosophy details.
8 | Text Box | 1 | MAK | NTS
9 | Callout | 1 | Julio.Aguilar | Source PFD to be indicated. Add arrow description