## 372-A-PID-57001-001-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Call-out | 1 | Ahmed Marhoon | General Comment for all P&IDs: Contractor to standardize the local indicators tagging with regard to Suffix. Normally if no DCS INDICATION tag exists, local indicator is tagged without a suffix. For this case no LI-1104 in DCS
2 | Callout | 1 | alexis.martinez | On Tank data block the Capacity shall be shown in “bbl” as per BMPS-A8
3 | Call-out | 1 | A.Jabbar Mahmood | Ensure that the proposed control scheme can handle the high pressure senarios i.e. when the pressure is above the set point
4 | Call-out | 1 | Mahdi Ali | This OPC is not connected to the stated PID.
5 | Text Box | 1 | Ahmed Marhoon | General comment: P&IDs to be updated post agreement on applications acceptable for wireless instruments. Currently, all instruments shown are wired type. Wireless signals representation shall be shown for applicable instruments in the next revisions based on the guidelines being developed at the JV for necessary standardization across BMP.
6 | Call-out | 1 | Ahmed Marhoon | Ensure both LIT-1104 & LIT-1105 have identical measuring Spans & Ranges. To achieve that, HP/LP Nozzles of both transmitters to be at the same heights.
7 | Call-out | 1 | RASHED SHOWAITER | TO CONFIRM SPECTACLE BLIND TO BE ON THE 1ST FLANGE (SHELL SIDE)
8 | Callout | 1 | Abdul Rahim | is this the correct symbol for Vacuum/pressure relief
9 | Call-out | 1 | Ahmed Ali | drain should be in the low side of the line
10 | Call-out | 1 | RASHED SHOWAITER | TO CONFIRM SPECTACLE BLIND TO BE ON THE 1ST FLANGE (SHELL SIDE)
11 | Callout | 1 | alexis.martinez | On Tank data block check capacity value which is not consistent with PFD and general arrangement information. 372-A-PFD-54001-001 and 372-D-GAD-57079 (4 sheets), respectively. Review and do the required corrections.
12 | Call-out | 1 | Ahmed Marhoon | Normally, isolation valves for the instrumentation connections are not shown on P&IDs. Those are part of hookups details.
13 | Callout | 1 | Abdul Rahim | and number
14 | Call-out | 1 | RASHED SHOWAITER | SPECTACLE BLIND
15 | Call-out | 1 | RASHED SHOWAITER | SPECTACLE BLIND
16 | Callout | 1 | alexis.martinez | On Tank data block the Tank Height is not matching with PFD 372-A-PFD-54001-001. Review and do the required corrections.
17 | Cloud+ | 1 | A.Jabbar Mahmood | They battery limit lines shall be shown in separate P&IDs
18 | Call-out | 1 | Mahdi Ali | Invalid reference
19 | Call-out | 1 | A.Jabbar Mahmood | Provide the drawing numbers of all incoming and outgoing streams - Typical
20 | Callout | 1 | alexis.martinez | What is the meaning of "IP-37207-L"? Is this a spec break?. The used symbol and abbreviation is not shown in BMPS-A-50003 Symbology sheets
21 | Text Box | 1 | Mahdi Ali | General Comments: 1. Use latest drawing border which is part of the Homogenization procedure. 2. This is a revamp drawing. MOC shall consult Bapco for allocating the line numbers within this set of PIDs 3. This is a revamp drawing. MOC shall consult Bapco for the drawing number. 4. Scale at the title block shall indicate: NTS. 5. Total Sheet number in the title block to have 3 digits, i.e. 001 6. Refer to BMPS-A8 section 6.3.2 for filling the title block of the PID. 7. Pump tag numbers to be verified.
22 | Callout | 1 | alexis.martinez | On Tank data block the units in brackets for Diameter and Height shall be shown in “mm” as per BMPS-A8
23 | Text Box | 1 | Ahmed Marhoon | General comment for unit 372 PID: Currently, two types of signals have been indicated on this P&ID for the control systems (Conventional 4-20 mA and FF). Contractor to confirm the right signal type in view of location of final control system (DCS) and update the P&ID accordingly. MOC to liaise with the JV to finalize the IO assignments and SRR/Control Room for unit 372.
24 | Callout | 1 | Ebrahim.Deyab | Use final numbering provided by Bapco.
25 | Call-out | 1 | Ahmed Marhoon | Contractor to review the suitability of Digital/Electronic Remote Sensors DP type level transmitters and evaluate the two types in terms of accuracy, ease of installation and maintenance and effects of ambient temperature on measurement. Applicable to LIT-1105 & LIT-1104.
26 | Cloud+ | 1 | 986131 | In the current arrangement shown the out breathing is through the RV's. Please review the requirement of a similar pilot operated vent valve for out breathing. Or provide dedicated Pressure vacuum breather valve to operate below the pressure set point of the emergency valves for out breathing.