## 372-A-PID-57002-001-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Call-out | 1 | 986131 | Review the pump capacity based on the revised Make-up required in the cooling tower. 3553+754= 4307 USgpm
2 | Callout | 1 | alexis.martinez | Review the suction pressure for pumps 372P0031A/B/C. The pump shall not be operating in vacuum.
3 | Call-out | 1 | Ahmed Marhoon | Local indicator at FV-1217 bypass to be added. also applicable for FV-1218/1332/1219/1220/1333.
4 | Callout | 1 | Ebrahim.Deyab | Verify the figure, basis on discharge and suction pressure
5 | Cloud+ | 1 | Khalid | Reverse arrow
6 | Cloud+ | 1 | 986131 | Follow BMPS A1 for abbreviation of UOM
7 | Cloud+ | 1 | Ebrahim.Deyab | Applicable to all pumps. Ensure pump suction and discharge valves are closed to pump ,reachable and safe for operation.otherwise consider installing isolation valves at suction and discharge adjacent to pump.
8 | Call-out | 1 | Ahmed Marhoon | Note1: Contractor to clarify how will the Headed status be sensed? Currently, the hardware/configuration provided is not sufficient to implement this logic.
9 | Callout | 1 | alexis.martinez | Review the suction pressure for pumps 372P0030A/B/C. The pump shall not be operating in vacuum.
10 | Call-out | 1 | Ahmed Marhoon | Contractor to clarify the SEQ numbers shown on P&IDs.
11 | Callout | 1 | alexis.martinez | For pumps 372P0031A/B/C, the data block shall follow the standard BMPS-A8. Correct the data block accordingly.
12 | Callout | 1 | alexis.martinez | For pumps 372P0030A/B/C, the data block shall follow the standard BMPS-A8. Correct the data block accordingly.
13 | Callout | 1 | Ebrahim.Deyab | Verify the figure, basis on discharge and suction pressure
14 | Call-out | 1 | Ahmed Marhoon | Add a note to the pumps to describe the overall pumps operation scheme (i.e. 1 operating, 1 standby and 1 spare). Applicable for the two pump sets on this sheet.
15 | Text Box | 1 | Ahmed Marhoon | General: Rotating equipment control and protection systems details (such as lubrication systems, MCM vibration, temperature ...etc) if specified in the next phase, shall be added to the P&ID set in Bapco's format.