## 372-D-DAT-57079-001-RB
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Call-out | 1 | Mahdi Ali | IS THIS DESIGN SPECIFICATION OR DATA SHEET. IF DATA SHEET THEN CHANGE THE TITLE AND IF DESIGN SPECIFICATION THEN CHANGE DOCUMENT TYPE FROM DAT TO TSP
2 | Cloud+ | 1 | Mohamed Ayyash | Project name / no. missing
3 | Cloud+ | 1 | Mohamed Ayyash | Project no. missing
4 | Cloud+ | 1 | Mohamed Ayyash | Should read 1/13. Why delete the page number on the cover page ?. Need to be consistent with BMP documents of which all consider the cover page as page one.
5 | Callout | 2 | Erwin.Lugue | Refer to BPMS-A1 sec 10.7.1
6 | Cloud+ | 2 | Khalid | Total 3 desal production once finalized.
7 | Cloud+ | 5 | Khalid | P3731/30 A/B/C
8 | Cloud+ | 5 | Khalid | Tank should be equipped with min flow of P3730/31/32 and min flow of U0020 considering tanks 276/7/8 are out of service.
9 | Cloud+ | 11 | Khalid | Capacity to be finalized.
10 | Text Box | 1 | MAK | General Comment: Use the latest cover sheet which is part of the Homogenization Procedure. TR shall coordinate with JV Directorate. | MOC will update cover sheet later, once received JVD/CLIENT instruction. | N
11 | Text Box | 1 | alexis.martinez | General: All Equipment Numbers need to be updated as per the new numbering provided by owner. | Equipment numbers are according equipment list. | N
12 | Cloud+ | 2 | Mohamed Ayyash | Align boxes with text for better representation | Agreed. | Y
13 | Cloud+ | 2 | Mohamed Ayyash | Align boxes with text for better representation | Agreed. | Y
14 | Text Box | 2 | Mahdi Ali | Align Text to avoid overlap | Agreed. | Y
15 | Text Box | 2 | Mahdi Ali | Change to 372-A-PID-00004-003 | Agreed. | Y
16 | Callout | 2 | alexis.martinez | Page 2. Tank capacity is not matching with PFD 372-A-PFD-54001-001. Review and do the required corrections. | Capacity shown on PFD is net working volume as indicated on note 4 instead maximum capacity. | N
17 | Callout | 2 | alexis.martinez | Page 2. Tank height is not matching with height on PFD 372-A-PFD 372-A-PFD-54001-001 and P&ID 372-A-PID-57001-001. Review and do the required corrections. | Height will be updated on next revision of PFD. 372D0079 box will be updated in next revision of PID. | N
18 | Callout | 2 | Abdul Rahim | power and Utilities | Agreed. | Y
19 | Callout | 3 | Abdul Rahim | all unit should be in SI | Units are in accordance with approved format. TTSJV is checking Owner comments related to format and will instruct accordingly to be implemented in all OC deliverables, if applicable. | N
20 | Text Box | 3 | Mahdi Ali | Requires proper formatting | Noted. | Y
21 | Callout | 4 | Abdul Rahim | all units should be in SI | Units are in accordance with approved format. TTSJV is checking Owner comments related to format and will instruct accordingly to be implemented in all OC deliverables, if applicable. | N
22 | Cloud+ | 5 | Mohamed Ayyash | Move to center of cell | Agreed. | Y
23 | Callout | 5 | alexis.martinez | Page 5. Include as per commented P&ID 372-A-PID-57001-001 and commented General arrangement 372-D-GAD-57079-001 (4 sheets), the number of nozzles and size | It is reflected. | Y
24 | Cloud+ | 5 | Mohamed Ayyash | Write "Datum" on one line. Adjust font or column width | Agreed. | Y
25 | Cloud+ | 5 | Mohamed Ayyash | Write "Dimension" and "Finish" on one line. Adjust font or column width | Agreed. | Y
26 | Cloud+ | 5 | Mohamed Ayyash | Write "schedule" on one line. Adjust font or column width | Agreed. | Y
27 | Cloud+ | 6 | Mohamed Ayyash | Move to center of cell | Agreed. | Y
28 | Callout | 6 | alexis.martinez | Pages 5 and 6. Move the sections 24,25,26,27 and 28 after section 23. Avoid split table 3 to insert section in between | Agreed. | Y
29 | Cloud+ | 6 | Mohamed Ayyash | Write "Dimension" and "Finish" on one line. Adjust font or column width | Agreed. | Y
30 | Cloud+ | 6 | Mohamed Ayyash | Write "schedule" on one line. Adjust font or column width | Agreed. | Y
31 | Callout | 8 | alexis.martinez | Page 8. The Tank Height is not matching with PFD and P&ID. Review and do the required corrections. | Height will be updated on next revision of PFD. 372D0279 box will be updated in next revision of PID. | N
32 | Text Box | 9 | Ahmed Marhoon | Location of nozzles for the level instruments shall be firmed post detail design/Hazop/SIL by the TTSJV taking into account the hold-up volume/surge volume and residence time specified for BMP. | Final location of nozzle will be confirmed later as comment indicates. | N
33 | Text Box | 9 | Ahmed Marhoon | Measuring range/span of both level transmitters shall be identical to avoid saturation and loss of control measurement/indication during abnormal condition. Location of the 2CNB Nozzle to be changed accordingly. | Note "Level transmitters for DCS and ESD in the same service shall have the same measuring range." will be included. | Y
34 | Text Box | 9 | Ahmed Marhoon | Nitrogen pressure control on this tank has been commented on the respective P&ID. Resolution on those comments to be reflected on the Data Sheet as applicable. | As per PID review, no change is required. | Y
35 | Callout | 9 | alexis.martinez | Page 5. Include as per commented P&ID 372-A-PID-57001-001 and commented General arrangement 372-D-GAD-57079-001 (4 sheets), the number of nozzles and size | It is reflected. | Y
36 | Text Box | 11 | Mahdi Ali | Inconsistent Tagging | Tag will be updated to D0278. | Y
37 | Callout | 11 | alexis.martinez | Page 11, Note 15. This is the revision A, hence empty notes are not used. | Note 15 will be used on next revision. | Y