## 372-D-GAD-57079-001-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Text Box | 1 | Ahmed Marhoon | 1. There is inconsistency between the P&ID and the tanks GAD with regard to the instrument nozzles e.g. missing nozzles for level transmitter with HH and LL alarms per P&ID. Contractor to cross check the instrument details on GAD with the P&ID. 2.Size of nozzles for the temperature gauges to be verified/confirmed by contractor with respect to BMPS-J2 and BMPS typical drawings (4 inch Vs 1.5 inc). 3. Location of nozzles for the level instruments shall be firmed post detail design/Hazop/SIL by the TTSJV taking into account the Hazop3/SIL recommendations, if any.
2 | Callout | 1 | Yousif Ahmadi | 100% per FEED data sheet
3 | Cloud+ | 1 | Khalid | 372D0279
4 | Callout | 1 | Yousif Ahmadi | 6.25mm per FEED datasheet
5 | Callout | 1 | Yousif Ahmadi | A 36/A106 Gr B
6 | Text Box | 1 | Mahdi Ali | Change the orientation of this drawing
7 | Cloud+ | 1 | 986131 | Drawing name and equipment name and number must appear on all pages of the drawing.
8 | Text Box | 1 | MAK | General Comment: Texts font style and size shall not be changed. Every drawing border is predefined with font style and size.
9 | Text Box | 1 | MAK | General Comment: The latest drawing borders have been submitted to JV Directorate on April 2018. Please use the latest drawing borders that are part of the Homogenisation Procedure.
10 | Cloud+ | 1 | Mohamed Ayyash | Move to center of cell
11 | Text Box | 1 | RASHED SHOWAITER | NX, 1, 12" stilling well pipe nozzle , 150# WN RF
12 | Cloud+ | 1 | Khalid | P3730A/B/C P3731A/B/C
13 | Call-out | 1 | 986131 | Please remove 0.73 and mention only note 33. As the figure there is misleading and has to be read with the note. A value to be assigned once after adding the hydrostatic pressure.
14 | Cloud+ | 1 | Khalid | RGDP