## 372-D-GAD-57079-003-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Call-out | 1 | RASHED SHOWAITER | 12" sch 10 stilling well pipe with radar gauge connection to measure the level of product inside the tank
2 | Cloud+ | 1 | RASHED SHOWAITER | access to the centre platfrom
3 | Call-out | 1 | RASHED SHOWAITER | add rail
4 | Text Box | 1 | Ahmed Marhoon | Contractor to check and confirm the location and service of nozzles 2CNA and 2CNB. According to the Nozzle Schedule, these nozzles are for Temp Gauges. However, the elevations of the nozzles seem to be incorrect. Also, According to the P&ID, there is only one TG on this tank which is assumed to be nozzle 1CN. If nozzles 2CN A/B are for the level measurement, then the elevations to be corrected. Check and confirm.
5 | Call-out | 1 | 986131 | Correct equipment number
6 | Cloud+ | 1 | Mohamed Ayyash | Move to center of cell
7 | Cloud+ | 1 | RASHED SHOWAITER | Need to be close to the platform and gauging platform
8 | Text Box | 1 | Ahmed Marhoon | Nozzles for the second level transmitter are missing from the schedule and GAD.
9 | Call-out | 1 | RASHED SHOWAITER | Nx
10 | Cloud+ | 1 | RASHED SHOWAITER | roof centre pin to be installed
11 | Text Box | 1 | 986131 | Show the working level of the tank.
12 | Cloud+ | 1 | 986131 | Show three nozzle as a minimum - 5NA,5NB,5NC - Refer BRA-69980 note 6.