## 372-G-DAT-50001-001-RA-CS
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Cloud+ | 1 | MAK | Use correct equipment tag no. Change on all pages to 372P3733A/B
2 | Text Box | 1 | Mahdi Ali | THIS DATASHEET TEMPLATE WAS REVISED AND WILL BE ISSUED WITH THE HOMOGENIZATION PROCEDURE. IN THE NEXT REVISION, THE REVISED TEMPLATE AND COVER PAGE SHALL BE USED.
3 | Cloud+ | 1 | MAK | Change on all pages to: BFW & CONDEN.DISTR(DEAERATOR)
4 | Call-out | 2 | Mohamed Aldoseri | Confirm the area classification as per the final hazardous area drawing-Typical
5 | Text Box | 2 | David.Jimenez | LV motors datasheets will be attached to MR as blank form to be filled in by Vendor during engineering, as they will be purchased under umbrella contract.
6 | Callout | 3 | A Albalooshi | API 610 compliant
7 | Callout | 3 | A Albalooshi | Please advise why hydraulic fit is not required. This was in FEED Data sheet
8 | Text Box | 3 | Isamu | Please refer to API 610 parag 6.4.2.3 and check if the minimum rating of 150# is allowable for an API pump
9 | Callout | 3 | A Albalooshi | Please advise why suction pressure regions designed for MAEP is not required. This was in FEED Data sheet
10 | Callout | 5 | A Albalooshi | Required as per FEED data sheets
11 | Callout | 5 | A Albalooshi | Required as per FEED data sheets