## 372-G-DAT-54001-001-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Text Box | 1 | Julio.Aguilar | Ensure the use of the project finalized cover page for the all data sheets. | Noted. The cover page will be updated in PO MDS. | Y
2 | Callout | 1 | Ebrahim.Deyab | Pumps number to be verified with final numbering. | Noted. It is changed to 370P0001A/B/C. | Y
3 | Text Box | 1 | seongjin.lee | The document is approved as Code 2 subject to incorporation of information obtained during subsequent detailed engineering development. Prior to issue of the PO the datasheet shall include all the updated details and be in code 2 approval status. | Noted. | Y
4 | Text Box | 1 | MAK | This datasheet template was revised and will be issued with the Homogenization Procedure. In the next revision, the revised template shall be used. | Noted. The cover page will be updated in PO MDS. | Y
5 | Text Box | 2 | Julio.Aguilar | Final figures shall be updated when the final hydraulic calculation is finalized | Noted. It will be updated in next revision. | N
6 | Cloud+ | 2 | Sameer.Ahmed | Indicate AVL as from approved vendor list | Noted. | Y
7 | Callout | 2 | Sameer.Ahmed | Insert the elec. area classification. As per note 3 of page 7 of 7, Electrical area classification was mentioned. | Noted. | Y
8 | Cloud+ | 2 | Sameer.Ahmed | Why "T3" is indicated while no electrical area classification is specified | Hazardous area classification is added. | Y
9 | Cloud+ | 3 | Sameer.Ahmed | Indicate AVL as from approved vendor list | No. Coupling AVL is only applicable for Hydraulic fit coupling. Thus it will be leave as blank. | N
10 | Text Box | 4 | hyunjin.paeng | AVL | Noted. | Y
11 | Cloud+ | 5 | Saeed Taher | Type of inspections for welds & castings shall be as per applicable codes. This is applicable to all pumps data sheets | It will be updated as per Inspection Class in next revision. | N