## 372-G-DAT-54015-001-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Text Box | 1 | Julio.Aguilar | Ensure the use of the project finalized cover page for the all data sheets.
2 | Cloud+ | 1 | Julio.Aguilar | Pump tag number to be as per last equipment list approved by project
3 | Text Box | 1 | seongjin.lee | The document is approved as Code 2 subject to incorporation of information obtained during subsequent detailed engineering development. Prior to issue of the PO the datasheet shall include all the updated details and be in code 2 approval status.
4 | Polyline Sketch to Scale | 2 | Julio.Aguilar | 5'-1"
5 | Callout | 2 | Julio.Aguilar | Final figures shall be updated when the final hydraulic calculation is finalized.
6 | Cloud+ | 2 | Julio.Aguilar | Rated flow shall be evaluated considering to empty the basin 372D0019 in 48 hr as per BOD. So the flow shall be revised in conjunction with the basin dimensions then when the basin dimension is completed the rated flow shall be revised to confirm the stated above.
7 | Callout | 2 | Ebrahim.Deyab | Remove u
8 | Cloud+ | 2 | Julio.Aguilar | Revise and confirm if this note apply here or confirm the appropriate note to be included.
9 | Cloud+ | 2 | Julio.Aguilar | There are not Note 19 and 20 in the list. Remove or add them in the list.
10 | Callout | 3 | Berik.Nurbolatov | Nozzle connection data should be provided fro the next revision.
11 | Callout | 3 | Berik.Nurbolatov | Please advise harness standard
12 | Callout | 4 | hyunjin.paeng | To be Deleted
13 | Cloud+ | 5 | Saeed Taher | Type of inspections shall be as per applicable codes
14 | Text Box | 6 | hyunjin.paeng | Sump Diameter
15 | Cloud+ | 6 | Julio.Aguilar | What is this?. Clarify
16 | Cloud+ | 7 | Julio.Aguilar | Remove
17 | Callout | 8 | Julio.Aguilar | Notes 19 and 20 are mentioned in the page 2, rows 48 and 58. Check and confirm if they are required
18 | Callout | 8 | Salman Jaffer | Please include Auto stop per FEED PID BRA-227167 sheet 19 of 54 (XHS 0302/0303)
19 | Callout | 8 | Julio.Aguilar | To be deleted