## 372-G-DAT-57002-001-RA-CS
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Text Box | 1 | MAK | This datasheet template was revised and will be issued with the Homogenization Procedure. In the next revision, the revised template shall be used.
2 | Text Box | 2 | Abdulaziz | Bearing housing & bearings shall be designed for oil mist lubrication in compliance to BMPS G8.
3 | Callout | 2 | alexis.martinez | GENERAL: For decimal separator use dot (.) instead of coma (,)
4 | Callout | 2 | Fernando.Perez | Change it for EQUIPMENT DATA SHEET
5 | Text Box | 2 | A.Jabbar Mahmood | General: Use decimal points instead of commas as decimal separator
6 | Callout | 2 | Fernando.Perez | Use capital "NOMINAL, change template in exceel
7 | Text Box | 2 | alexis.martinez | GENERAL: Review pumps calculations. The data is not matchming with FEED, neither with EPC P&ID data block
8 | Callout | 2 | Fernando.Perez | Check Group.
9 | Callout | 2 | alexis.martinez | Page 2, rows 33/34. Inconsistency of maximum ambient temperature and relative humidity shown in page 2 and page 8. Review and correct
10 | Call-out | 2 | Abdulaziz | Shall consider summer peak time temprature
11 | Callout | 2 | alexis.martinez | Review pump capacity as per revised make-up revised in the cooling tower.
12 | Callout | 2 | alexis.martinez | Vacuum suction pressure is not allowed. Review the suction pressure.
13 | Cloud+ | 2 | Mohamed Ayyash | Cooling water is the stream name and not the source. Need to specify the plant where it is coming from.
14 | Text Box | 2 | Abdulaziz | API 610 edition shall be indicated
15 | Text Box | 3 | Abdulaziz | Pump DBSE shall be greater than the cartridge seal length to facilitate insitu seal repair
16 | Callout | 3 | Berik.Nurbolatov | Should be updated for the next revision.
17 | Callout | 3 | Fernando.Perez | Flanged & Valved Acc BMPS-G2 & BMPS-SD-G-10289
18 | Callout | 3 | Fernando.Perez | Baseplate Acc GD-G1368-0
19 | Callout | 3 | Fernando.Perez | Coupling Guard Required Acc BMPS-G2
20 | Text Box | 3 | Abdulaziz | ISO VG 68 shall be considered as an option.
21 | Call-out | 3 | Abdulaziz | Bearing housing & bearings shall be designed for oil mist lubrication in compliance to BMPS G8.
22 | Text Box | 4 | Abdulaziz | Bearings temperature shall be included
23 | Call-out | 5 | Abdulaziz | Yes
24 | Callout | 5 | Fernando.Perez | Acc Feed Data Sheet most of the test marked as observed should be witnessed Inspection Level 3. & Acc 2520-z000-PP611_0 the criticality Ranking is C (Insp.Level 3).Check
25 | Callout | 5 | Erwin.Lugue | Equivalent weight in S.I. units to be provided
26 | Text Box | 6 | Abdulaziz | Typo
27 | Callout | 7 | Fernando.Perez | Accelerometer Required for motor Acc BMPS-A3 Parag.8.5
28 | Callout | 7 | Fernando.Perez | Instrumentation for driver shall be Acc BMPC-A3 / G2 & API 670
29 | Callout | 7 | Fernando.Perez | Check Group should be Group II
30 | Cloud+ | 9 | Ahmed.Marhoon | A clarification required from Contractor for deleting technical notes from Datasheet. One of the notes was regarding requirement of instrumentation scope which has been excluded in the new revision. Also, the system to capture requirements for the instrumentation and control scope on relevant RFI documents, to be discussed and agreed with the Contractor.
31 | Callout | 9 | Fernando.Perez | Change redaction to: NPSHr shall be less than NPSHa at lesat in 1.4 m(4 ft)
32 | Callout | 9 | Fernando.Perez | Driver to be sized to cover End Of Curve
33 | Text Box | 9 | Abdulaziz | Minimum flow by pass shall be reviewed for these pumps
34 | Text Box | 9 | Abdulaziz | M/SEAL vendor shall be provided with operating parameter during, start-up/shutdown mode, study state condition an upset in order to provide the optimum design selection.