## 372-J-INX-57001-001-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Text Box | 1 | Ahmed.Marhoon | 10. Add a note to the List stating that all missing/blank fields will be filled with the necessary data once available post detail engineering.
2 | Text Box | 1 | Ahmed.Marhoon | 9. General: Service descriptions of the main instruments and the associated accessories to be identical.
3 | Text Box | 1 | Ahmed.Marhoon | 1.The Instrument List generated at this stage of the project (with IBD) is considered preliminary. It is the Contractor's responsibility to update the list post detail engineering to include packages details, Hazop3 recommendations, SIL recommendations, TCQs resolutions ... etc.
4 | Text Box | 1 | Ahmed.Marhoon | 3. Contractor to carry out a thorough consistency check to identify and resolve any duplication/errors in instrument details (such as instrument service).
5 | Text Box | 1 | Ahmed.Marhoon | 13. Instruments tag numbers, with regard to standardization of suffixes, related to motors (pumps, MOVs ...etc) such as local/remote and 50ft switches to be updated based on the latest typicals as indicated on TCQ 000-JTSQ-000009-001.
6 | Text Box | 1 | Ahmed.Marhoon | 15. Current Sorting is by Loop Name, which is acceptable. However, MOC to coordinate with JVD to ensure a common system is followed by all OCs
7 | Text Box | 1 | Ahmed.Marhoon | 2. Orifice Plates common for multiple transmitters, if any, (DCS/DCS and DCS/ESD) to be provided with a clarification note in Remarks to state that the orifice plate is COMMON for the respective transmitters. Also Contractor to coordinate with the JVD to standardize on a common approach for naming/tagging of these orifice plates. Should they be mainly assigned with DCS loop number or the ESD.
8 | Text Box | 1 | Ahmed.Marhoon | 18. If applicable, all ESD related soft tags, such as RESET, INHIBIT switches ...etc, to be considered. In addition, any hard switches to also be included.
9 | Text Box | 1 | Ahmed.Marhoon | 14. Instrument Manufacture and Instrument Model Columns are missing from the list/report. To be added. MOC to coordinate with JVD for standardization.
10 | Text Box | 1 | Ahmed.Marhoon | 8. It is understood that the MOVs, RVs and Rupture Disks data sheets will be created by TTSJV in SPI data base. However, since these are non-instrument items per Owner's system; these items to be excluded from the Instrument List. Only instrument accessories (such as switches on MOVs) required for the monitoring and control signals to be included in the Instrument List. This is a common requirement for all OCs and hence MOC is requested to coordinate with the JVD for for the necessary guidance and standardization.
11 | Text Box | 1 | Ahmed.Marhoon | 12. If specified, details of equipment surveillance and protection systems such as MCM to be updated based on vendor's design.
12 | Text Box | 1 | Ahmed.Marhoon | 4. If applicable, Details of GAS and FAS to be updated post detail engineering and mutual agreement on segregation or integration of the systems as being discussed/evaluated at the JVD with Owner.
13 | Text Box | 1 | Ahmed.Marhoon | 7. As agreed at JVD, Sight Glasses will be tagged with special piping tag number and hence shall not be included in the Instrument List. MOC to coordinate with the JVD for for the necessary guidance and standardization.
14 | Text Box | 1 | Ahmed.Marhoon | 19. Contractor to confirm that the type (RTD/Thermocouple) of temperature element indicated in the list meets the required accuracy and process requirements.
15 | Text Box | 1 | Ahmed.Marhoon | 17. As a standard approach, non-wired instruments such as PGs, TGs, LGs etc shall have no loops assigned to. No â€œDUMMY LOOPSâ€ are needed in such cases.
16 | Text Box | 1 | Ahmed.Marhoon | 11. Local indicators tag numbers with regard to the suffix philosophy to be updated post closure of the comment captured on P&IDs. Due to different interpretations of the BMPS-J3 relevant clause and standard practice; MOC is requested to coordinate with the JVD for for the necessary guidance and standardization.
17 | Text Box | 1 | Ahmed.Marhoon | 16. Junction Boxes and any other cabinets can be included in the Index. These are wiring equipment and are available under PANELS. However, MOC to coordinate with JVD for the necessary guidance and standardization.
18 | Text Box | 1 | Ahmed.Marhoon | 6. Equipment tag numbers to include plant-prefix to ensure consistency with the approach followed on P&IDs. MOC may coordinate with JVD for the necessary guidance and standardization.
19 | Cloud+ | 1 | Mohamed Ayyash | Unit name/number missing
20 | Text Box | 1 | Ahmed.Marhoon | 5. Instrument tag numbers to be updated based on the comments provided on the IBD P&ID. For instance, switches tag numbers to be regularized as commented on the P&ID.
21 | Cloud+ | 2 | Ahmed.Marhoon | These are part of System Description User Defined Table (UDT) and cannot be included under the 'instrument Location' table
22 | Call-out | 2 | Ahmed.Marhoon | General: To ensure homogenization across all OCs, MOC to coordinate with JVD to reflect the latest index descriptions/definitions as agreed with Owner's SPI Representative.
23 | Cloud+ | 2 | Ahmed.Marhoon | These are part of System Description User Defined Table (UDT) and cannot be included under the 'instrument Location' table
24 | Cloud+ | 2 | Ahmed.Marhoon | These are part of System Description User Defined Table (UDT) and cannot be included under the 'instrument Location' table
25 | Text Box | 2 | Omran A | PRESSURE SWING ADSORPTION
26 | Cloud+ | 2 | Ahmed.Marhoon | These are part of System Description User Defined Table (UDT) and cannot be included under the 'instrument Location' table
27 | Call-out | 4 | Ahmed.Marhoon | INSTRUMENT TYPE: a- For typical Instrument Names such as Dual Temperature elements shall have the same loop number. b- Instrument Tags such as ZSL-xxxx/ZSH-xxxx shall be given Z loop Names and not U Loop Names. c- Instrument Tags such as XSV-xxxx shall be given X loop Names and not U Loop Names. d- Instrument Tags such as HS-xxxx shall be given H loop Names and not U Loop Names e- Loop Names for ESD tagging shall be revised.
28 | Call-out | 4 | Ahmed.Marhoon | INSTRUMENT SERVICE: Equipment on the Instrument Service shall also be prefixed with Unit No.
29 | Call-out | 4 | Ahmed.Marhoon | EQUIPMENT: All missing Equipment shall be filled in
30 | Cloud+ | 4 | Ahmed.Marhoon | General: align logos appropriately.
31 | Call-out | 4 | Ahmed.Marhoon | LINE: No consistency in allocating Line Numbers to instruments Shall only be limited to Flow Elements, Flow Meters, Control Valves and TWs
32 | Call-out | 4 | Ahmed.Marhoon | General: Variable area flow indicator tag number shall be changed from Fl to FIC.
33 | Call-out | 4 | Ahmed.Marhoon | STATUS: a - Shall be all changed to â€œPROPOSEDâ€ b- B/V BY VENDOR is not on the SPI STATUS table and hence to be removed. It can be added under the REMARKS
34 | Cloud+ | 4 | Ahmed.Marhoon | To be clarified
35 | Call-out | 4 | Ahmed.Marhoon | INSTRUMENT LOCATION: All missing Locations shall be filled in
36 | Text Box | 5 | Abdul Majeed | General comment: for soft tag instrument location to be DCS e.g. FC; DCS Controller
37 | Cloud+ | 5 | Ahmed.Marhoon | General: Contractor to ensure validity and accuracy of information reflected in the index. The P&ID reference shall be according to the latest revision.