## 372-J-INX-57002-001-RA-CS
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Text Box | Page 1 | MAK | General Comment: This is not the latest document template. For all documents, use the latest document template that is part of the Homogenisation Procedure.
2 | Cloud+ | Page 1 | Mohamed Ayyash | Unit name/number missing
3 | Text Box | Page 1 | Ahmed.Marhoon | 1. The I/O list generated at this stage of the project (with IBD) is considered preliminary. It is the Contractor's responsibility to update the list post detail engineering to include packages details, Hazop3 recommendations, SIL recommendations, TCQs resolutions ... etc.
4 | Text Box | Page 1 | Ahmed.Marhoon | 2. If applicable, details of GAS and FAS to be updated post detail engineering and mutual agreement on segregation or integration of the systems as being discussed/evaluated at the JVD with Owner Representatives.
5 | Text Box | Page 1 | Ahmed.Marhoon | 3. If applicable, IBD I/O lists to include preliminary details of Segments Segregation per BMPS-J7. In next revisions (IDD1, IDD2 ... etc post Hazop); the segmentations to be updated based on the criticality levels assigned for each control loop post Risk Assessment and Loop Criticality for Segment Loading.
6 | Text Box | Page 1 | Ahmed.Marhoon | 4. SRR building number to be updated to reflect the latest numbers and format assigned for the respective Satellite Rack Room.
7 | Text Box | Page 1 | Ahmed.Marhoon | 5. MOC to coordinate with the JVD to standardize the format of I/O list. This is a standard document that will be generated by all OCs and it is recommended to follow a common format to ensure homogenization across BMP.
8 | Text Box | Page 1 | Ahmed.Marhoon | 6. FEED revision contained details that are now excluded from the EPC IBD revision. Details such as interface signals between systems covering Serial Communications have been excluded from the list. Contractor to clarify.
9 | Text Box | Page 1 | Ahmed.Marhoon | 7. I/O list to be updated to include Wireless Instruments in case considered in the next phase for the non-critical instruments.
10 | Text Box | Page 1 | Ahmed.Marhoon | 8. In addition to the universal tables included in the I/O list, Contractor to add breakdown tables detailing the I/O estimations for packages and major equipment such as compressors and heaters.
11 | Callout | Page 3 | Mohamed Ayyash | REDUNDANT
12 | Cloud+ | Page 3 | Ahmed.Marhoon | Replace "DEVICE" with "DETECTOR"
13 | Call-out | Page 3 | Ahmed.Marhoon | FEED Revision listed other abbreviations too. Since this section is common for all I/O lists that will be generated by all OCs, MOC to coordinate with JVD to include standard comprehensive ABBREVIATIONS in the I/O lists to cover all applicable abbreviations.
14 | Cloud+ | Page 3 | Ahmed.Marhoon | Missing from table.
15 | Cloud+ | Page 4 | Ahmed.Marhoon | General: Contractor to advise the rationale for specifying some I/Os as NON-IS at this stage of the project. Per BMPS-J2; generally Intrinsically Safe equipment shall be used wherever possible with explosion proof being used only when IS equipment is not available.
16 | Cloud+ | Page 4 | Ahmed.Marhoon | Contractor to clarify the AIR and the values indicated under this type of Analog Inputs.
17 | Cloud+ | Page 4 | Ahmed.Marhoon | Contractor to review and update the ESD related I/Os. Contractor to clarify the rationale for limiting the signals related to ESD to REDUNDANT type only.
18 | Cloud+ | Page 4 | Ahmed.Marhoon | Add a clarification note to finalize these details based on selected equipment supplier.
19 | Cloud+ | Page 4 | Ahmed.Marhoon | Contractor to clarify the AOR and the values indicated under this type of Analog Outputs.
20 | Cloud+ | Page 4 | Ahmed.Marhoon | SRR No. to be included
21 | Cloud+ | Page 5 | Ahmed.Marhoon | Contractor to review and confirm if the F&G system is required for unit 372 or not based on the final Unit's Fire & Gas Equipment List.
22 | Cloud+ | Page 5 | Ahmed.Marhoon | Replace "INTERPOSITION" with "INTERPOSING".
23 | Cloud+ | Page 6 | Ahmed.Marhoon | Where is this included?
24 | Call-out | Page 6 | Ahmed.Marhoon | The estimated 3 FF Multiplexers to be reviewed and confirmed by Contractor as it looks like under estimated. Also, confirm FF for unit 372?
25 | Call-out | Page 6 | Ahmed.Marhoon | 10 I/O count for AI-MX to be reviewed and confirmed by the Contractor as it looks under estimated.
26 | Call-out | Page 6 | Ahmed.Marhoon | Preliminary estimation to be added to the list. Final signals to be confirmed at a later stage.
27 | Call-out | Page 6 | Ahmed.Marhoon | But why excluded from the table? Needs to be standardized as agreed with JVD.