## 372-S-DAT-54003-001-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Text Box | 1 | Julio.Aguilar | Ensure the use of the project finalized cover page for the all data sheets.
2 | Call-out | 1 | Mahdi Ali | Incorrect document type
3 | Text Box | 1 | seongjin.lee | The document is approved as Code 2 subject to incorporation of information obtained during subsequent detailed engineering development. Prior to issue of the PO the datasheet shall include all the updated details and be in code 2 approval status.
4 | Text Box | 1 | Jeung.Kim | This data sheet has to be updated based on the updating of related utility summary- typical comment
5 | Cloud+ | 1 | Julio.Aguilar | Update as per last approved equipment list for the unit 370. Review and apply this in the whole document.
6 | Callout | 5 | Ebrahim.Deyab | Conductivity figure at FEED is 10 uS/cm, keep it as it is.
7 | Cloud+ | 5 | Julio.Aguilar | Reword as: N beds in service for 100% flow, one bed in regeneration and one bed as spare
8 | Cloud+ | 6 | Julio.Aguilar | Check if "By Others" is to be change from here.
9 | Cloud+ | 6 | Julio.Aguilar | Confirm whether neutralization water pumps are condensate polishing mixed bed package MFR scope
10 | Callout | 9 | Dowon Pyun | Contractor to confirm if the following requirements are unnecessary to be specified; - Pressure condition - Suspended solid condition
11 | Callout | 11 | Ebrahim.Deyab | Change "Lines" to Mixed Beds MB.
12 | Callout | 13 | Ebrahim.Deyab | Mention the package name.
13 | Callout | 14 | Ebrahim.Deyab | N beds in service 100%, one bed in regeneration and one bed as spare.
14 | Callout | 17 | Julio.Aguilar | in latest stage of the project
15 | Text Box | 18 | JaiMun.Oh | The external surface shall be painted as per BMPS-B5. Insulation shall be performed as per BMPS-N1.
16 | Callout | 18 | Dowon Pyun | The use of plastic piping should as per BMP standard
17 | Callout | 19 | Dowon Pyun | Contractor to recheck the subjected PFD no. and updated as per last approved of PFD numbering for the project and MSDs accordingly
18 | Cloud+ | 19 | Julio.Aguilar | Indicated the PID numbers
19 | Callout | 19 | Dowon Pyun | To be modified as "Major Project Specifications but not limited to;"